## Active Project List
MTEP16 SPM Active Project List 2016-06-30
PrjID | Prj_Rec_Date | Target Appendix | App ABC | Region | Geo Location by TO Member System | Project Name | Project Description | Min Expected ISD | Max Expected ISD | Sum of Estimated Cost | System_Need | Need Date | Alternatives | State | State2 | Min Plan Status | Preliminary Allocation FF | Preliminary Share Status | Other_Type | Max kV | Min kV | Miles New | Miles Upgrade | Facility Count | MISO Facility | Member Project ID | Submitting Company | Transmission Project Type | Planning Review Status
3005 | 2016-04-28 | A in MTEP16 | B>A | Central | AmerenIL | S. Belleville-Tilden Terminal Equipment Upgrade | Baldwin 138 kV Substation - Construct a 5 position 138 kV ring bus at Baldwin Substation (5 - 3000 A, 40 kA PCBs). Build a 138 kV double-circuit line between Baldwin Substation and the tap to the South Belleville-Tilden 1526 138 kV line by rebuilding 2 miles of existing single-circuit 138 kV line to double-circuit capability, both circuits to have 2000 A summer emergency capability. | 2017-06-01 | 2017-06-01 | 3400000 | Increased Reliability (IR) project. Improve reliability at the Baldwin 138 kV Bus and on the South Belleville-Tilden 138 kV line. |  |  | IL | IL | Proposed | BaseRel |  |  | 138 | 0 | 2 | 0 | 2 | Y | AMRN38 | Ameren Services Company | Bottom-Up | Submitted for Recommendation
7820 | 2015-12-14 | A in MTEP16 | B>A | Central | AmerenIL | Hennepin-Kewanee-6101 Reconductoring | Upgrade terminal equipment at Hennepin terminal. | 2017-06-01 | 2017-06-01 | 300000 | Age and condition | 2016-12-01 |  | IL | IL | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
7860 | 2015-09-11 | A in MTEP16 |  | Central | AmerenIL | Effingham 138-Effingham NW Increase Ground Clearance | Effingham 138-Effingham, Northwest 138 kV Line - Elevate 2.72 miles of 954 kcmil ACSR conductor to permit operation at 120 degrees C. Upgrade terminal equipment at Effingham 138 Substation. | 2016-06-01 | 2016-06-01 | 2000000 | The existing line conductor would be loaded to about 130% of its rating following the outage of the Newton-Casey-1 and Mv. Vernon, West-Xenia-1 345 kV lines in 2015 summer, based on 2014 analysis work. | 2016-06-01 |  | IL | IL | Proposed | BaseRel |  |  | 138 | 0 | 0 | 2.72 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
7869 | 2016-05-23 | A in MTEP16 | B>A | Central | AmerenIL | Alsey Tap (Ballard) Breaker Station | Install 138 kV breaker station near tap to the PPI Alsey Plant on the Jersesyville, Northwest-Meredosia-1 138 kV line. May be an ultimate 6-breaker ring bus. | 2016-05-01 | 2016-05-01 | 6626495 | PPI initiated project |  |  | IL | IL | M5_In Service | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9261 | 2016-05-23 | A in MTEP16 |  | Central | AmerenIL | Searitt Breaker Station | Build a 3-breaker 138 kV ring bus (Searitt Breaker Station) adjacent to the N. Decatur-Latham-1566 138 kV line near the planned Enbridge Pumping Station. Buld a radial 138 kV line to the new customer substation. | 2016-06-01 | 2017-12-01 | 4563667 | Establish connection to customer load. | 2017-12-01 |  | IL | IL | Planned | Other |  | Reliability | 138 | 0 | 0.5 | 0 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9722 | 2016-05-23 | A in MTEP16 |  | Central | AmerenIL | Frederick, North 138-69 kV Transformer Replacement | Replace existing 138-69 kV transformer bank with 112 MVA unit. | 2016-10-03 | 2016-10-03 | 0 | Needed to serve local load | 2016-10-03 | None | IL | IL | Proposed | Other |  | Reliability | 138 | 69 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9726 | 2016-02-02 | A in MTEP16 |  | Central | AmerenIL | Fogarty 138-34.5 kV Transformer Connection | Provide 138 kV connection to supply 138-34.5 kV transformer | 2018-06-01 | 2018-06-01 | 1726448 | Needed to serve local load | 2018-06-01 | None | IL | IL | Proposed | Other |  | Distribution | 138 | 34.5 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9727 | 2016-05-23 | A in MTEP16 |  | Central | AmerenIL | Wakefield Substation | Establish 138 kV ring bus; connect to South Bloomington-Clinton-1372 line to supply Wakefield Substation | 2019-06-01 | 2019-06-01 | 7430056 | Needed to serve local load | 2019-06-01 | None | IL | IL | Proposed | Other |  | Distribution | 138 | 34.5 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9736 | 2016-01-13 | A in MTEP16 |  | Central | AmerenIL | East Quincy-Hamilton-4 Reconductoring | Replace existing conductor | 2016-05-01 | 2016-05-01 | 8315916 | Age and condition of facilities | 2015-12-05 | None | IL | IL | M5_In Service | Other |  | Condition | 138 | 138 | 0 | 30.61 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9741 | 2016-03-11 | A in MTEP16 |  | Central | AmerenIL | E. Collinsville-Porter Road Terminal Equipment Upgrade | Upgrade terminal equipment at Porter Road | 2016-05-24 | 2016-05-24 | 50000 | Conductor overload following concurrent outage of two 345 kV lines. | 2016-06-01 | None | IL | IL | M5_In Service | Other |  | Reliability | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9845 | 2015-09-14 | A in MTEP16 |  | Central | AmerenIL | Gallatin 138 kV Ring Bus | Construct 138 kV ring bus | 2017-05-01 | 2017-05-01 | 5621250 | Local load serving need | 2017-05-01 | None | IL | IL | Proposed | Other |  | Distribution | 138 | 69 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9853 | 2016-05-20 | A in MTEP16 |  | Central | AmerenIL | Mt. Vernon, West Terminal Equipment | Upgrade terminal equipment in Prairie State-Mt. Vernon, West position | 2017-06-01 | 2017-06-01 | 0 | Age and conditions of facilities | 2017-06-01 |  | IL | IL | Proposed | Other |  | Condition | 345 | 345 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9869 | 2016-05-20 | A in MTEP16 |  | Central | AmerenIL | Havana-Springfield 138 kV Upgrade | Upgrade terminal equipment | 2017-06-01 | 2017-06-01 | 0 | Age and condition of facilities |  |  | IL | IL | Proposed | Other |  | Condition | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
9873 | 2016-05-20 | A in MTEP16 |  | Central | AmerenIL | Edwards 138-69 kV Transformer Addition | Install 138-69 kV Transformer | 2016-12-01 | 2016-12-01 | 0 | Local load serving need |  |  | IL | IL | Proposed | Other |  | Reliability | 138 | 69 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10884 | 2016-03-11 | A in MTEP16 |  | Central | AmerenIL | Roxford Substation - Replace 345/138 kV Transformer | Roxford 345/138 kV Substation - Replace 345/138 kV, 560 MVA transformer with a 700 MVA unit, and install a 3000 A, 50 kA PCB to place the transformer on its own position at Roxford Substation. | 2016-05-23 | 2016-05-23 | 3611589 | P3-2: Overload to existing transformer following concurrent line and generator outage. | 2016-06-01 |  | IL | IL | M5_In Service | BaseRel |  |  | 345 | 138 | 0 | 0 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10904 | 2016-03-18 | A in MTEP16 |  | Central | AmerenIL | Brokaw-Gibson City South-1582 Reconductoring | Rebuild to 1200 A summer emergency capability. Upgrade line terminal equipment at Gibson City South Substation. | 2016-12-01 | 2016-12-01 | 10318299 | Age and condition | 2016-12-01 |  | IL | IL | Planned | Other |  | Condition | 138 | 0 | 0 | 28.5 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
11063 | 2016-04-19 | A in MTEP16 |  | Central | AmerenIL | Rising-North Champaign-1592 Terminal Upgrade | Upgrade terminal equipment at Rising Substation on the Rising-North Champaign-1592 138 kV line position. | 2016-12-01 | 2016-12-01 | 1747553 | Age and condition of existing equipment | 2016-12-01 |  | IL | IL | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10483 | 2015-12-16 | A in MTEP16 |  | Central | AmerenMO | Cape-Kelso-2 and Kelso-Miner-2 - Increase Ground Clearance | Increase ground clearance to and perform line hardware verification to permit operation at 120 degrees C. Upgrade terminal equipment at Cape, Kelso, and Miner Substations. | 2016-12-01 | 2016-12-01 | 5586082 | Age and condition of facilities | 2016-12-01 |  | MO | MO | Planned | Other |  | Condition | 161 | 161 | 0 | 25.84 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10604 | 2016-05-20 | A in MTEP16 |  | Central | AmerenMO | Page-Sioux-4 Reconductoring | Replace 14.28 miles of 2-300 kcmil Copper conductor with conductor matching or exceeding the capability of the rest of the line (954 kcmil ACSR conductor) | 2016-12-01 | 2016-12-01 | 0 | Age and condition of existing conductor. |  |  | MO | MO | Proposed | Other |  | Condition | 138 | 0 | 0 | 14.28 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10687 | 2016-02-03 | A in MTEP16 |  | Central | AmerenMO | Barrett Station 138-12.47 kV Transformer Connection | Provide connection for 2nd. 138-12.47 kV transformer at Barrett Station Substation. | 2022-06-01 | 2022-06-01 | 0 | Local load serving need |  |  | MO | MO | Planned | Other |  | Distribution | 138 | 12.47 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Recommendation
10162 | 2016-06-16 | A in MTEP16 |  | Central | CWLD | McBaine Line Terminal Upgrades | Upgrade McBaine-McBaine Tap line to 249 MVA (300501 bus). Replace a switch (from 600 A to 1200 A) and a wave trap (from 600 A to 2000 A). Limiting element will be conductor at 895 A = 249 MVA. | 2016-03-01 | 2016-03-01 | 50000 | AECI asked for increased rating on this line to accommodate contingencies identified in their internal planning. | 2016-06-01 |  | MO | MO | Proposed | Other |  | Reliability | 161 | 0 | 0 | 0 | 1 | Y |  | City of Columbia, MO | Bottom-Up | Submitted for Recommendation
2873 | 2015-10-06 | A in MTEP16 |  | Central | DEI | Danville E. 69kV looped feed | Construct new Danville East substation near HRH hospital - single 22.4MVA transformer - 6945 ckt to be looped through | 2018-06-01 | 2018-06-01 | 990000 | distribution capacity | 2018-06-01 | none required or needed | IN | IN | Proposed | Other | Not Shared | Distribution | 69 | 12 | 0.5 | 0 | 1 | NT | DIN0216 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9834 | 2015-10-30 | A in MTEP16 |  | Central | DEI | Noblesville to Tipton W. 230kV Rebuild | Noblesville to Tipton West 23008 ckt: Replace all single/H-frame pole structures with steel poles, reconductor with 954ACSR45X7 OVAL / OPGW and build Switching Station with 3-2000A line switches near existing Carmel 146th St. junction. | 2018-12-31 | 2018-12-31 | 12079985 | This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to faulty insulators and galloping issues due to lines positioning. | 2018-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 230 | 0 | 0 | 12 | 1 |  | AMIN1055 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9850 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Lebanon Prairie Crk. 69kV Switching Station | New Lebanon Prairie Crk. 69kV Switching Station to be inserted in the 6983 ckt. | 2016-12-31 | 2016-12-31 | 3518244 | Lebanon Muni (IMPA member) is adding 2 new distribution subs and this switching station is required to supply an additional transmission delivery point. | 2016-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Distribution | 69 | 0 | 1.1 | 0 | 1 |  | AMIN1129 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9854 | 2015-09-17 | A in MTEP16 |  | Central | DEI | Speed 138kV - Brkr Replacements | Speed 138kV - Replace OCB 13850, 13857, 13869, 13881, 138138 TIE and obsolete relays on CIR 13850, 13857, 13881. | 2017-12-31 | 2017-12-31 | 2264125 | These breakers have been identified by Duke's R&I Planning group for replacement due to continual reliability problems, mtc costs, and risk of significant OM cost to extend service life and are part of the D-Oil Breaker Replacement Reliability Program. | 2017-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  | AMIN1407 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9855 | 2015-11-30 | A in MTEP16 |  | Central | DEI | Columbus North Brkr / Relay Replacements | Columbus North: Replace OCB 6975, 6929, 69230-1, 6950 and obsolete relays on CIR 6929, 6950, 6975, 6982. Also replace relays on CIR 23019. | 2020-12-31 | 2020-12-31 | 2711016 | These breakers have been identified by Duke's R&I Planning group for replacement due to continual reliability problems, mtc costs, and risk of significant OM cost to extend service life and are part of the D-Oil Breaker Replacement Reliability Program. | 2020-12-31 |  | IN | IN | Proposed | Other |  | Condition | 230 | 69 | 0 | 0 | 1 |  | TIN1422 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9856 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Walton 230-69kV Brkr Replacements | Walton: Replace OCB 69 KV CAP BK, 69230-1, 69110, 69 KV TRANSFER, 6927, 6987, 23020-21. | 2017-12-31 | 2017-12-31 | 3303866 | These breakers have been identified by Duke's R&I Planning group for replacement due to continual reliability problems, mtc costs, and risk of significant OM cost to extend service life and are part of the D-Oil Breaker Replacement Reliability Program. | 2017-12-31 |  | IN | IN | Proposed | Other |  | Condition | 230 | 69 | 0 | 0 | 1 |  | TIN1406 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9858 | 2016-01-25 | A in MTEP16 |  | Central | DEI | Bedford 345 Brkr / Xfmr Replacements | Bedford 345: Replace 345/138kV Bank 7; Replace relays on CIR 6995, 13829, 13837, 34506, 34521. Replace all 69kV and 138kV Oil Circuit Breakers. | 2018-12-31 | 2018-12-31 | 12078813 | These breakers and transformer Bk 7 have been identified by Duke's R&I Planning group for replacement due to continual reliability problems, mtc costs, and risk of significant OM cost to extend service life and are part of the D-Oil Breaker Replacement Reliability Program. | 2018-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 345 | 69 | 0 | 0 | 2 |  | TIN1469 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9888 | 2015-09-14 | A in MTEP16 |  | Central | DEI | MiddleFork to Deer Crk. Jct. 69kV rebuild | Rebuild 6988 ckt. from MiddleFork sub to deadend 879/1041-01 and from Deer Cr Jct to 879/1046. 477acsr@120C w/ OPGW - 187 wood poles to be replaced with light duty steel. | 2017-12-31 | 2017-12-31 | 4860632 | This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to outdated poles, obselete and poor performing static, and old construction type. | 2017-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 7.1 | 1 |  | TIN1528 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9889 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Sharpsville to Kokomo SE 69kV rebuild | Rebuild 69174 ckt. from Sharpsville sub to Kokomo SE. 477acsr@120C w/ OPGW - 174 wood poles to be replaced with light duty steel. | 2017-12-31 | 2017-12-31 | 4287945 | This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to outdated poles, obselete and poor performing static, and old construction type. | 2017-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 7.3 | 1 |  | TIN1530 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9890 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Gibson Sta. to Merom Sta. 345kV Deadend Structures | Gibson to Merom: Install (10) double deadend structures in the 34511 ckt. | 2017-12-31 | 2017-12-31 | 4433734 | This line has been identified by Duke's R&I Planning group for reducing cascading structural failure exposure. | 2017-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 345 | 0 | 0 | 0 | 1 |  | TIN1536 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9891 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Flat Rock to Hope Jct. 69kV Pole Replacements | Flat Rock to Hope Jct. 6975 ckt. pole replacements (45), replace line switches at both ends. Transfer existing conductor to new poles. | 2016-12-31 | 2016-12-31 | 1087274 | This line has been identified by Duke's R&I Planning group for pole replacement due to age at 60 to 80 years old. | 2016-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 3.3 | 1 |  | TIN1534 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9892 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Lewis Crk. to Flat Rock 69kV Pole Replacements | Lewis Crk. to Flat Rock 6975 ckt. pole replacements (100), replace line switches at Lewis Crk with 1200A. Transfer existing conductor to new poles. | 2017-06-01 | 2017-06-01 | 1875342 | This line has been identified by Duke's R&I Planning group for pole replacement due to age at 60 to 80 years old. | 2017-06-01 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 5.7 | 1 |  | TIN1533 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9893 | 2015-09-14 | A in MTEP16 |  | Central | DEI | Shelbyville Northeast CB and Relay Replacements | Shelbyville Northeast - Replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | 2017-06-01 | 2017-06-01 | 3511433 | These breakers have been identified by Duke's R&I Planning group for replacement due to continual reliability problems, mtc costs, and risk of significant OM cost to extend service life and are part of the D-Oil Breaker Replacement Reliability Program. | 2017-06-01 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 138 | 69 | 0 | 0 | 1 |  | TIN1581 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9897 | 2015-09-15 | A in MTEP16 |  | Central | DEI | River Ridge Gateway 138-12kV New Sub. | River Ridge Gateway 138-12kV Sub. to be inserted in the 13857 ckt. between Clark Maritime and HE Northport | 2018-06-01 | 2018-06-01 | 1000000 | Load Growth in the Clarksville area | 2018-06-01 | No cost effective alternatives | IN | IN | Proposed | Other |  | Distribution | 138 | 12 | 0 | 0 | 1 |  | DIN1393 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9905 | 2015-11-30 | A in MTEP16 |  | Central | DEI | Sharpsville to Windfall Jct. 69kV rebuild | Rebuild 69174 from Sharpsville sub to Windfall Jct - 477acsr@120C w/ OPGW - 81 wood poles to be replaced with light duty steel. Replace (3) Windfall Jct switches with 1200A. Install new motor mechs on 69-1 and 69-3 at Windfall Junction. | 2017-12-31 | 2017-12-31 | 2179983 | This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to outdated poles, obselete and poor performing static, and old construction type. | 2017-12-31 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 3.5 | 1 |  | TIN1529 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9914 | 2015-10-26 | A in MTEP16 |  | Central | DEI | Mohawk to Lee Hanna 69kV rebuild | Rebuild 5.84 mile 69kV - 69130 ckt. from Mohawk to Mohawk Ind. Jct to Lee Hanna Jct with 954ACSR@120C - replace (2) Lee Hanna Jct line switches with 1200A | 2017-06-01 | 2017-06-01 | 3741298 | Load Growth in the Hamilton-Hancock Co. areas - study will be provided. | 2017-06-01 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 5.84 | 1 |  | TIN1609 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9926 | 2015-09-15 | A in MTEP16 |  | Central | DEI | Spelterville 138-34kV Sub Expansion | Spelterville: expand sub footprint, Install 138/34kV 60MVA Bank | 2017-06-01 | 2017-06-01 | 1000000 | Wabash River 34kV source bank is being retired due to poor condition and the load is being transferred to this location. | 2017-06-01 | No cost effective alternatives | IN | IN | Proposed | Other |  | Condition | 138 | 34 | 0 | 0 | 1 |  | DIN1620 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
10144 | 2015-09-30 | A in MTEP16 |  | Central | DEI | Cayuga Station 230kV Breakers Replace | Cayuga Gen. Sta.: Replace existing 230kV OCBs 23011-03, 23013-11,230B9-13 and associated disconnect switches. New brkrs will be 3000 amp, 63KIA with 3000A disc switches. | 2017-12-31 | 2017-12-31 | 1536000 | NERC TPL-001-4, R2.3 and R2.8 Breaker Short Circuit Interrupting Duty Deficiencies. |  | No cost effective alternatives | IN | IN | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | TIN1640 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
11343 | 2016-06-07 | A in MTEP16 |  | Central | DEI | Lafayette SE to General Foods Jct 13808 Reconductor | Lafayette SE to General Foods Jct 13808 Reconductor: rebuild 0.64 mile of 138kV line with 954acsr@120C | 2018-06-01 | 2018-06-01 | 1060000 | MTEP16 study results - Cat. P1 violation caused by the combination of three things: (1) 13876 outages at the Laf. 230 end, (2) load forecast of stations in the path from Laf. SE to Staley to Concord Rd to Rea Magnet to Alcoa to Laf. 230, and (3) MTEP project 9246 / DEI project TIN1607 - New Laf SE 138kV ckt. | 2018-06-01 | Existing facility short term rating for the worst case MTEP16 scenario is 123.4MVA for 12 minutes. Operating mitigation: load shed required - open Concord Rd 13808-76 breaker. This mitigation can be improved in the near term by resolving an apparent ROW encroachment. | IN | IN | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0.64 | 1 |  | TIN1923 | Duke Energy Corporation | Bottom-Up | Submitted for Recommendation
9220 | 2015-06-23 | A in MTEP16 |  | Central | IPL | Parker Substation Breaker Replacements | Replacement of three (3) 138 kV breakers at Parker Substation; Two line breakers for the 132-07 and 132-17 transmission lines and a bus-tie breaker. | 2018-12-31 | 2018-12-31 | 0 | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8. |  |  | IN | IN | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 3 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
9221 | 2015-06-23 | A in MTEP16 |  | Central | IPL | Southport Substation Breaker Replacement | Replacement of one (1) 138 kV breaker at Southport Substation; One line breaker for the 132-29 transmission line. | 2016-12-31 | 2016-12-31 | 0 | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8. |  |  | IN | IN | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
9222 | 2015-06-23 | A in MTEP16 |  | Central | IPL | Thompson 138 kV Substation Breaker Replacements | Replacement of three (3) 138 kV breakers at Thompson 138 kV Substation; Two line breakers for the 132-68 and 132-77 transmission lines and a bus-tie breaker. | 2016-12-31 | 2016-12-31 | 0 | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8. |  |  | IN | IN | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 3 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
9223 | 2015-06-23 | A in MTEP16 |  | Central | IPL | River Road Substation Breaker Replacement | Replacement of one (1) 138 kV breaker at River Road Substation; One bus-tie breaker. | 2018-12-31 | 2018-12-31 | 0 | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8. |  |  | IN | IN | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
9602 | 2015-09-03 | A in MTEP16 |  | Central | IPL | Mooresville Substation Breaker Replacements | Replacement of three (3) 138 kV breakers at Mooresville Substation; Two (2) line breakers for the 132-84 and 132-24 lines and a bus-tie breaker. | 2016-12-31 | 2016-12-31 | 0 | J238 GIP and results of annual short circuit analysis; NERC TPL-001-4 requirements R2.3 and R2.8. | 2016-12-31 |  | IN | IN | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 3 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
11123 | 2016-04-26 | A in MTEP16 |  | Central | IPL | Guion Relay Addition | Addition of redundant bus differential (87) relay at Guion 345 kV south bus section. | 2017-07-15 | 2017-07-15 | 0 | Addition of redundant relay at Guion to mitigate specific P55 contingency violations that were previously mitigated with MISO MTEP15 Projects #9403 and #9404. Due to the addition of this project to mitigate this violation, Projects #9403 and #9404 are withdrawn. |  |  | IN | IN | Planned | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Recommendation
9563 | 2015-09-01 | A in MTEP16 |  | Central | PPI | Cronus 138 kV Transmission Lines | Construct two new 138 kV transmission lines from Ameren Illinois's West Tuscola substation to serve new Cronus Fertilizer Plant | 2017-12-01 | 2017-12-01 | 3600000 | New Cronus Fertilizer Plant near Tuscola, IL will have an estimated 40 MW peak load. It is located in Eastern Illini Electric Cooperative and will be served by PPI. The customer has requested that it be served with two independent transmission feeds. | 2017-12-01 |  | IL | IL | Planned | Other |  | Reliability | 138 | 0 | 6 | 0 | 2 |  | 2016-13 | Prairie Power, Inc. | Bottom-Up | Submitted for Recommendation
9564 | 2015-09-14 | A in MTEP16 |  | Central | PPI | Turris Tap Breaker Station, Turris-Athens 138 kV, Athens 138/69 kV station | Construct Turris tap 138 kV 4-breaker station, Turris-Athens 138 kV transmission line, Athens 138/69 kV substation, Athens Tap 69 kV switching station | 2019-12-01 | 2020-12-01 | 16297000 | This project will provide an alternate feed to serve Turris Coal and Menard Electric Cooperative's Athens Substation and relieve loading on the East Lanesville 138/69 kV transformer. This project will allow Turris Coal to be feed from the east, i.e. from Latham or Lanesville as well as from the west via Elkhart Tap, i.e. Havana and East Springfield. It would also provide a backup source to Turris Coal from the 69 kV system. | 2019-12-01 |  | IL | IL | Planned | Other |  | Reliability | 138 | 69 | 5 | 0 | 4 |  | 2016-12,38,39,43 | Prairie Power, Inc. | Bottom-Up | Submitted for Recommendation
4393 | 2016-05-19 | A in MTEP16 | B>A | Central | Vectren | Y67-2 Dubois - Huntingburg Rebuild | Rebuild and Reconductor approx. 3.5 miles of 69 kV | 2018-12-31 | 2018-12-31 | 2625000 | Aging Infrastructure. | 2018-12-31 | Build a new line | IN | IN | Planned | Other |  | Condition | 69 | 0 | 0 | 3.54 | 1 | Y | 2013SIGE7 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9940 | 2016-04-01 | A in MTEP16 |  | Central | Vectren | Elliott Dist Sub and Y52 69kV Line Loop | New Distribution Substation with 9.375MVA 69kV/12kV transformer and Y52 69kV loop from Elliott sub to Sunbeam sub for load growth | 2015-12-31 | 2015-12-31 | 1350000 | Other Project - Distribution | 2015-12-31 |  | IN | IN | M2a_Pre-Project Approval | Other |  | Distribution | 69 | 12 | 0 | 0 | 2 |  | 2016SIGE1 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9942 | 2016-06-16 | A in MTEP16 |  | Central | Vectren | Z85 138kV Line Relocation for Road Widening | Public Roadway relocation of 1.25 miles of Z85 138kV line | 2016-12-31 | 2016-12-31 | 1200000 | Other Project - Relocation | 2016-12-31 |  | IN | IN | Proposed | Other |  | Economic | 138 | 0 | 0 | 0 | 1 |  | 2016SIGE2 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9946 | 2016-05-18 | A in MTEP16 |  | Central | Vectren | Adams Substation for Distribution | 69kV/12kV distribution substation to serve customer load (Y65). | 2018-12-31 | 2018-12-31 | 2100000 | Serve customer load. | 2018-12-31 |  | IN | IN | Proposed | Other |  | Reliability | 138 | 12 | 0 | 0 | 1 |  | 2016SIGE11 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9948 | 2016-05-18 | A in MTEP16 |  | Central | Vectren | Y56 69kV Line Rebuild from Pelzer to Chrisney | 69kV line Y56 rebuild from Pelzer to Chrisney substations. | 2019-12-31 | 2019-12-31 | 6800000 | Aging infrastructure. | 2019-12-31 |  | IN | IN | Proposed | Other |  | Condition | 69 | 0 | 0 | 0 | 1 |  | 2016SIGE11 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9952 | 2016-05-19 | A in MTEP16 |  | Central | Vectren | Y43 Berry Plastics Sub Loop Feed | Berry Plastics Substation loop feed (69kV Y43). | 2018-12-31 | 2018-12-31 | 300000 | Enhanced customer service reliability. | 2018-12-31 |  | IN | IN | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | 2016SIGE13 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Recommendation
9543 | 2016-03-30 | A in MTEP16 |  | East | CETO | Stamping Plant 138 kV Circuit Breaker Replacement | Increase short-circuit capacity of the 177 and 188 circuit breakers | 2016-06-30 | 2016-06-30 | 560000 | Short-circuit analysis has identified that these breakers would be expected to interrupt fault currents in excess of their capability. | 2016-06-30 |  | MI | MI | M5_In Service | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9544 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Annual Breaker Replacement Program - 2017 | CE Breaker Replacement Program - 2017 | 2017-12-31 | 2017-12-31 | 1240000 | Replace breakers that are defective, damaged, or fail testing parameters to improve system reliability and address safety concerns. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9545 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Annual Breaker Replacement Program - 2016 | Breaker Replacement Program for 2016 | 2016-12-31 | 2016-12-31 | 1380000 | Replace breakers that are defective, damaged, or fail testing parameters to improve system reliability and address safety concerns. | 2016-12-31 |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9859 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Line Equipment Replacement Program - 2016 | Replace cross arms, insulators, guying, and switches as needed to maintain the lines' condition | 2016-12-31 | 2016-12-31 | 160000 | Replace line equipment that is defective or damaged to maintain line performance, reduce outages, address code clearance, and/or address safety concerns. | 2015-12-31 |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9860 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Line Equipment Replacement Program - 2017 | Replace cross arms, insulators, guying, and switches as needed to maintain the lines' condition | 2017-12-31 | 2017-12-31 | 160000 | Replace line equipment that is defective or damaged to maintain line performance, reduce outages, address code clearance, and/or address safety concerns. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9861 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Pole Replacement Program - 2016 | Replace damaged or defective poles with new poles | 2016-12-31 | 2016-12-31 | 360000 | Replace wood poles that fail testing parameters or are found to be damaged to improve system reliability and address safety concerns. | 2016-12-31 |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9862 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Pole Replacement Program - 2017 | Replace damaged or defective poles with new poles | 2017-12-31 | 2017-12-31 | 680000 | Replace wood poles that fail testing parameters or are found to be damaged to improve system reliability and address safety concerns. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9863 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Line Sag Remediation - 2016 | Install poles or replace spans of conductor to remediate sag limits | 2016-12-31 | 2016-12-31 | 400000 | Consumers Energy's recently completed LiDAR inspection indicated various locations where the sag limits would be less than the flows identified in planning assessments and/or expected operating scenarios | 2016-12-31 |  | MI | MI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9865 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Relay Replacement Program - 2016 | Replace electromechanical and/or defective relays with new digital relays | 2016-12-31 | 2016-12-31 | 240000 | Improve protective system performance by replacing electromechanical relays with digital relays and replacing protective relays that are defective, damaged, or fail testing parameters. | 2016-12-31 |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9866 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Relay Replacement Program - 2017 | Replace electromechanical and/or defective relays with new digital relays | 2017-12-31 | 2017-12-31 | 480000 | Improve protective system performance by replacing electromechanical relays with digital relays and replacing protective relays that are defective, damaged, or fail testing parameters. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9868 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Substation Equipment Replacements - 2016 | Replace damaged or defective substation equipment, not including breakers or relays, with new equipment | 2016-12-31 | 2016-12-31 | 560000 | Replace substation equipment that is defective, damaged, or fails testing parameters to improve system reliability and address safety concerns. | 2016-12-31 |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9870 | 2015-09-14 | A in MTEP16 |  | East | CETO | CE Substation Equipment Replacements - 2017 | Replace damaged or defective substation equipment, not including breakers or relays, with new equipment | 2017-12-31 | 2017-12-31 | 500000 | Replace substation equipment that is defective, damaged, or fails testing parameters to improve system reliability and address safety concerns. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9871 | 2016-05-20 | A in MTEP16 |  | East | CETO | Edenville-Edenville Jct 138 kV Line Rebuild - North | Rebuild the north portion of the Edenville-Edenville Jct 138 kV Line, approximately 9.8 miles, utilizing 138 kV single circuit construction and 336.4 ACSR conductor. | 2017-12-31 | 2017-12-31 | 4170000 | Line is constructed with KK71 towers and copper line conductor that date to the early 1920's. This line has experienced below average outage performance over the last 5 years. Experience with these style and vintage of tower has shown significant ground level rusting which will lead to tower failure and line outages. This project will also remediate numerous sag limits identified by LiDAR studies. |  |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 9.8 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9872 | 2016-05-20 | A in MTEP16 |  | East | CETO | Edenville-Edenville Jct 138 kV Line Rebuild - South | Rebuild the south portion of the Edenville-Edenville Jct 138 kV Line, approximately 2.0 miles, utilizing 138 kV single circuit construction and 336.4 ACSR conductor. | 2016-12-31 | 2016-12-31 | 850000 | Line is constructed with KK71 towers and copper line conductor that date to the early 1920's. This line has experienced below average outage performance over the last 5 years. Experience with these style and vintage of tower has shown significant ground level rusting which will lead to tower failure and line outages. This project will also remediate numerous sag limits identified by LiDAR studies. |  |  | MI | MI | Planned | Other |  | Condition | 138 | 0 | 0 | 2 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9874 | 2015-09-14 | A in MTEP16 |  | East | CETO | Cole Creek Spur 138 kV Line Rebuild | Rebuild the Cole Creek-Cole Creek Jct 138 kV Line, approximately 4.7 miles, utilizing 138 kV single circuit construction and 795 ACSR conductor. | 2017-12-31 | 2017-12-31 | 1960000 | Line is constructed with KK71 towers and copper line conductor that date to the early 1920's. This line has experienced below average outage performance over the last 5 years. Experience with these style and vintage of tower has shown significant ground level rusting which will lead to tower failure and line outages. This project will also remediate numerous sag limits identified by LiDAR studies. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 0 | 0 | 4.7 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9875 | 2016-06-28 | A in MTEP16 |  | East | CETO | Chase 138 kV Bus Rebuild | Rebuild the 138 kV portion of Chase Substation to a three breaker ring bus | 2017-12-31 | 2017-12-31 | 3200000 | The Chase Substation 138 kV bus is projected to be overloaded during an outage of the Cobb-Felch Road 138 kV Line followed by an outage of the Four Mile-Piston Ring 138 kV Line during shoulder peak load levels. Chase Substation is designed as a single bus, single breaker station; a ring bus will improve reliability, allowing for breaker maintenance without interruption of the transmission network. | 2017-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
9878 | 2015-09-14 | A in MTEP16 |  | East | CETO | Vrooman - Complete 138 kV Bus | Complete the 138 kV bus as a ring by adding one 138 kV breaker | 2018-06-01 | 2018-06-01 | 800000 | Increase reliability of the transmission system by completing the ring bus. Vrooman Substation is designed as a future ring; however, it is presently operated as a straight bus. Required breaker maintenance cause interruption of the transmission network and reduces reliability to distribution customers. | 2018-06-01 |  | MI | MI | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
10046 | 2015-09-17 | A in MTEP16 |  | East | CETO | Beaver Creek Customer Interconnection | Consumers Energy has received a request to connect a new load near Grayling. Construct a 138 kV three breaker ring bus at Beaver Creek Substation. Replace relaying at Higgins Substation. | 2018-03-01 | 2018-03-01 | 3500000 | New customer load. Due to the need to maintain high-speed clearing on the Higgins-Beaver Creek 138 kV Line, a 138 kV line tap cannot be accommodated; circuit breakers at Beaver Creek are required. Additionally, relays at Higgins Substation need replaced to accommodate the new configuration. |  |  | MI | MI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 2 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Recommendation
10763 | 2016-05-04 | A in MTEP16 |  | East | CETO | J392 Generation Upgrades-CE | Add a wavetrap and upgrade relaying at Emmet Substation to accommodate the addition of a dual-pilot relay scheme on the Emmet-Livingston 138 kV Line. | 2016-06-17 | 2016-06-17 | 874000 | The dual-pilot scheme was identified in studies of J392 in the MI-Feb15-DPP cycle. | 2016-06-17 |  | MI | MI | M5_In Service | GIP | Not Shared |  | 138 | 0 | 0 | 0 | 1 |  |  | Consumers Energy Transmission Owner | Externally Driven | Recommended
9685 | 2015-09-10 | A in MTEP16 |  | East | ITCT | Jacob - St. Clair 120 kV Sag Remediation | Remediate the Sag Limit on Jacob-St. Clair 120 kV to 292 MVA (1405 Amp) | 2019-12-31 | 2019-12-31 | 139000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Jacob – St. Clair 120 kV circuit. The worst limiting sag rates this circuit at 228 MVA (1095 Amp) for summer normal and emergency ratings. The sag limit on this 120 kV line is projected to overload for a shutdown-plus-contingency or double-circuit-tower outage that takes out both Boyne – St. Clair and Golf – St. Clair 120 kV lines. | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_016 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9692 | 2015-09-10 | A in MTEP16 |  | East | ITCT | Seneca - Spokane 120 kV Sag Remediation | Remediate the Sag Limit on Seneca-Spokane 120 kV to 283 MVA (1362 Amp) | 2018-12-31 | 2018-12-31 | 339000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Seneca – Spokane 120 kV circuit. The worst limiting sag rates this circuit at 213 MVA (1025 Amp) for summer normal and emergency ratings. The sag limit on this 120 kV section is projected to overload for a breaker fault at Troy’s “HF” position during peak condition. Several double-circuit-tower contingencies involving Bloomfield – Troy 120 kV circuit also cause this line to overload. |  |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_022 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9883 | 2015-09-14 | A in MTEP16 |  | East | ITCT | Ironton 120 kV-Install Two Line Breakers | Install two 120 kV breakers to terminate the two River Rouge–Ironton 120 kV connections at Ironton | 2019-12-31 | 2019-12-31 | 910000 | The Ironton area is projected to experience low voltage and a 120 kV section between Ironton and Ironton-Navarre-Riverview tap will be heavily overloaded for a shutdown-plus-contingency that takes out both River Rouge feeds into Ironton. The main cause of these thermal and voltage violations is that the contingency also takes out two of the three 120/24kV distribution transformers at the station, causing the remaining one to draw too much VARs that consequently overloads the 120 kV section from Ironton-Navarre-Riverview tap | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_025 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9884 | 2015-09-14 | A in MTEP16 |  | East | ITCT | Belle River - Pontiac 345 kV Sag Remediation | Raise the Sag Limit on Belle River-Pontiac 345 kV to 1414 MVA (2366 Amp) | 2019-12-31 | 2019-12-31 | 340000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Belle River – Pontiac 345 kV circuit. The worst limiting sag rates this circuit at 1157 MVA (1936 Amp) for summer normal and emergency ratings. The sag limit on this 345 kV line is projected to overload for a shutdown-plus-contingency or double-circuit-tower outage that takes out both Pontiac – Fitz and Blackfoot – Fitz 345 kV lines | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  | ITC_15_015 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9885 | 2015-09-14 | A in MTEP16 |  | East | ITCT | Jewell - St. Clair #1 345 kV Sag Remediation | Raise the Sag Limit on Jewell-St.Clair 345 kV to 1965 MVA (3288 Amp) | 2019-12-31 | 2019-12-31 | 5380000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Jewell – St. Clair 345 kV circuit. The worst limiting sag rates this circuit at 1610 MVA (2694 Amp) for summer normal and emergency ratings. The sag limit on this 345 kV line is projected to overload for a shutdown-plus-contingency or double-circuit-tower outage that takes out Belle River – St. Clair and St. Clair – Stephens 345 kV lines | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  | ITC_15_017 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9887 | 2015-09-14 | A in MTEP16 |  | East | ITCT | Pontiac - Wixom 345 kV Sag Remediation | Raise the Sag Limit on Pontiac-Wixom 345 kV to 1185 MVA (1983 Amp) | 2019-12-31 | 2019-12-31 | 305000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Pontiac – Wixom 345 kV circuit. The worst limiting sag rates this line at 997 MVA (1669 Amp) for summer normal and emergency ratings. The sag limit on this line is projected to overload a shutdown-plus-contingency that takes out both Blackfoot – Madrid and Placid – Pontiac 345 kV lines | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  | ITC_15_019 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9900 | 2015-09-15 | A in MTEP16 |  | East | ITCT | River Rouge - Ironton #2 120 kV Sag Remediation | Raise the Sag Limit on River Rouge-Ironton #2 120 kV to 271 MVA (1304 Amps) | 2018-12-31 | 2018-12-31 | 340000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the River Rouge – Ironton 120 kV circuit. The worst limiting sag rates this circuit at 172 MVA (828 Amp) for summer normal and emergency ratings. The sag limit on this 120 kV line is projected to overload for a shutdown-plus-contingency that takes out Navarre–Adelaide–Ironton and River Rouge – Ironton #1 120 kV lines | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_020 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9902 | 2015-09-15 | A in MTEP16 |  | East | ITCT | Sterling 120 kV Ring Bus | Install a new 120 kV bus and one 120 kV breaker to convert Sterling to a ring bus. Also move the Sterling transformer #201 connection to the new bus and install a disconnect switch on the low side. Breaker “HT” will become the bus-tie between bus #101 and #104 | 2018-12-31 | 2018-12-31 | 1100000 | ITC Michigan annual assessment has identified thermal overloads along the Northeast–Sloan–Sterling 120 kV line when there is a fault on Sterling breaker “HF”, taking out buses 101 and 102. As a result, only the source at Northeast is left to feed the string of load along the Northeast-Sloan-Sterling 120 kV line thereby overloading the circuit during peak and shoulder peak conditions. The sensitivity models (70/30 load forecast) also show voltage issues under the same breaker fault contingency | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_030 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9994 | 2015-12-04 | A in MTEP16 |  | East | ITCT | Custer - Monroe 120 kV Line Rebuild | Rebuild the entire Custer – Monroe 120 kV line. Pre-build it to 230 kV construction to facilitate possible future 230 kV expansion in southern Michigan. Replace all existing structures and conductor with new double-circuit structures that are designed for bundled 954 ACSR 54/7 conductor and install this conductor along with an OPGW path. Also, upgrade terminal equipment at Custer and Monroe | 2019-12-31 | 2019-12-31 | 14500000 | The Custer - Monroe 120 kV line is projected to become overloaded for the suspension of Units 1, 2, and 3 at Whiting in combination with several different types of shutdown plus contingencies, with the most severe loadings resulting from the outage of two transmission lines. More specifically, the highest loadings on this line are projected to occur for the outage of any combination of two of the three 345 kV lines at the Monroe 3-4 switchyard, which will leave only one 345 kV line and the path formed by Transformer 304 and this 120 kV line as outlets for the power generated from Units 3 and 4 at Monroe. The sole 345 kV line at Monroe 3-4 that remains in-service will not be a strong enough sink to prevent the Custer – Monroe 120 kV line from becoming overloaded. The only operating solution that is available is to back down the Monroe Units 3 and 4. These issues were first identified in the Whiting Attachment Y analysis and verified by MISO during the MTEP 2013 process. Due to the complexity of the solutions studied, the issues were tabled for further analysis in MTEP 2014. The result of this analysis was the approved MTEP14 project to reconfigure the Custer – Whiting 120 kV line into Monroe to create a second line from Custer to Monroe as well as a third 120 kV sink from Monroe to Whiting. Although the three 120 kV lines plus an additional 345 kV line in the Monroe 3-4 switchyard constitute an infrastructure that is fully capable of supporting the maximum output produced by Units 3 and 4 when the two other 345 kV lines in the Monroe 3-4 switchyard are out-of-service, the problem is that routing the lines to Monroe would be difficult because there are wetlands, a highway, bodies of water, and limited room in the remaining areas. Further routing studies would need to be done to ensure that the appropriate ROW would exist for the new structures that would be installed in these areas. | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 0 | 1 |  | ITC_15_007 | ITC Transmission | Bottom-Up | Submitted for Recommendation
9998 | 2015-09-15 | A in MTEP16 |  | East | ITCT | 2017 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs | 2017-12-31 | 2017-12-31 | 47970000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 120 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
9999 | 2015-09-15 | A in MTEP16 |  | East | ITCT | 2018 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | 2018-12-31 | 2018-12-31 | 53250000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 120 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10000 | 2015-09-15 | A in MTEP16 |  | East | ITCT | 2019 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | 2019-12-31 | 2019-12-31 | 53310000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 120 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10010 | 2016-03-23 | A in MTEP16 |  | East | ITCT | ITCT Customer Interconnections - Year 2019 | Customer interconnection requests and retirements. | 2019-12-31 | 2019-12-31 | 2000000 | Customer interconnection requests and retirements. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Distribution | 120 | 0 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10243 | 2015-10-16 | A in MTEP16 |  | East | ITCT | Navarre 120 kV Breakers HX Replacement | Upgrade the existing Navarre 120 kV breaker HX to have an interrupting capability of 50 kA. | 2018-06-30 | 2018-06-30 | 70000 | The Navarre 120 kV breaker HX is at risk of having to interrupt faults as high as 101% of its capability. | 2018-06-30 |  | MI | MI | Proposed | Other |  | Reliability | 120 | 0 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10270 | 2016-01-27 | A in MTEP16 |  | East | ITCT | Apache – Seneca 120 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Apache – Seneca 120 kV line to 230 MVA (1107 Amp). | 2018-12-31 | 2018-12-31 | 202000 | A National Electric Safety Code (NESC) sag-clearance study was performed to inspect the Apache – Seneca 120 kV circuit. The worst limiting sag rates this circuit at 175 MVA (842 Amp) for summer normal and emergency ratings. The sag limit on this 120 kV section is projected to overload for a breaker fault at Troy’s “HF” position during peak condition. A double-circuit-tower outage that takes out Bloomfield – Wheeler and Bloomfield – Troy 120 kV circuits also causes this line to overload. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 120 | 0 | 0 | 0 | 1 |  | ITC_15_053 | ITC Transmission | Bottom-Up | Submitted for Recommendation
10425 | 2015-12-01 | A in MTEP16 |  | East | ITCT | J340 Generation Interconnection | Rebuild 5.3 miles of the existing 120 kV Cosmo tap to double circuit steel poles, relocate the Harvest Wind tap point, and string 954 ACSR to create the new J340-Harvest Wind-Grassmere 120 kV line. Expand the Grassmere station and install 1-345 kV breaker, a 345/120 kV transformer, and a 120 kV breaker on the low side of the transformer to tie in the new line. | 2017-09-01 | 2017-09-01 | 15150000 | TO Network Upgrades and Interconnection Facilities required to accommodate the J340 Generation Interconnection Request in the MISO Queue. | 2017-09-01 |  | MI | MI | Under Construction | GIP | Shared |  | 345 | 120 | 0 | 5.3 | 3 |  |  | ITC Transmission | Externally Driven | Recommended
10723 | 2016-02-10 | A in MTEP16 |  | East | ITCT | Skylark | ITC will install 2-120 kV line breakers and 2-120 kV section breakers with associated disconnects at Skylark, and loop the 120 kV Northeast-Sloan line in and out. OPGW will be added on the new Northeast-Skylark and Sloan-Skylark 120 kV lines, and relay upgrades will occur at Sloan and Northeast. | 2017-12-01 | 2017-12-01 | 5395000 | Accommodate a load interconnection request submitted by DTE Energy. | 2017-12-01 |  | MI | MI | Planned | Other |  | Distribution | 120 | 0 | 0.2 | 7.7 | 5 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10923 | 2016-03-21 | A in MTEP16 |  | East | ITCT | ITCT Pole Top Switch Additions/Replacement Program 2017 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | 2016-12-31 | 2016-12-31 | 2400000 | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 120 | 0 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
10924 | 2016-03-21 | A in MTEP16 |  | East | ITCT | ITCT Pole Top Switch Additions/Replacement Program 2018 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | 2018-12-31 | 2018-12-31 | 2400000 | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 120 | 0 | 0 | 0 | 1 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
11003 | 2016-04-12 | A in MTEP16 |  | East | ITCT | Mercury Interconnection | Construct a new 120 kV,3 breaker substation and install approx. 0.8 miles of new double circuit structures to loop the existing Artic-Crestwood 120 kV line into the new substation. Install approx. 4.7 miles of OPGW (fiber) on the Arctic-Ranger line and upgrade relaying at Crestwood and Ranger. | 2017-12-01 | 2017-12-01 | 10100000 | Accommodate a new load interconnection request from DTE in Dearborn, MI. | 2017-12-01 |  | MI | MI | Planned | Other |  | Distribution | 120 | 0 | 1.6 | 4.7 | 6 |  | ITC_16_001 | ITC Transmission | Bottom-Up | Submitted for Recommendation
11043 | 2016-04-15 | A in MTEP16 |  | East | ITCT | Relay Modifications at Monroe to Accommodate PJM Y1-069 Lallendorf Generator Interconnection | Perform necessary relay modifications and install a new wave trap at Monroe in order to accommodate the PJM generator interconnection request ID# Y1-069 (in the PJM queue) which involves the construction of a new 799 MW natural gas generation facility in First Energy. | 2016-04-04 | 2016-04-04 | 250000 | Facilitate the interconnection of a new 799 MW natural gas facility in northern Ohio. | 2016-04-04 |  | MI | MI | M5_In Service | Other |  | Distribution | 345 | 0 | 0 | 0 | 1 |  | ITC_13_052 | ITC Transmission | Bottom-Up | Submitted for Recommendation
11443 | 2016-06-28 | A in MTEP16 |  | East | ITCT | Ranger Interconnection Request | ITC to install 2-3000 A, 120 kV, 40 kA min. int. capability, line breakers at existing Ranger Station. DTE to replace existing transformers with 40 MVA 120/13.2 kV transformers. Upgrades will support 50MW of new load at Ranger, and 37 MW of load relocated from Ford Engineering distribution station. Trainers on the River Rouge - Warren #2 line will also be upgraded to prevent overload. | 2017-12-01 | 2017-12-01 | 2173000 | Accommodate interconnection request from DTE. | 2017-12-01 |  | MI | MI | Planned | Other |  | Reliability | 120 | 0 | 0 | 0 | 4 |  |  | ITC Transmission | Bottom-Up | Submitted for Recommendation
9864 | 2016-05-02 | A in MTEP16 |  | East | ITCT, METC | Whiting - Custer 120 kV Rebuild | Rebuild 9.98 miles of 636 ACSR from the Whiting – Custer 120 kV circuit using 1431 ACSR and OPGW on new 230 kV future double circuit structures. Replace limiting equipment at both the Whiting and Custer stations | 2018-10-01 | 2018-10-01 | 14300000 | The Whiting – Custer 120 kV circuit is projected to severely overload under various contingency scenarios, the worst involving the double circuit tower outage of the Morocco-Milan-Monroe and Monroe – Lalendorf (Y1-069) 345 kV circuits. The overloads were identified in the 2015 ITCTransmission/METC Near Term (2020) Assessment in both the peak and off-peak load level models. The overloads are projected to occur with flows from IESO to ITCT and vice versa. | 2018-10-01 | Proposal 2: Lulu 345 kV Station Install a new 345 kV switching Station (Lulu) and cut in the 3-ended Morocco – Milan – Monroe 345 kV circuit, thus creating the Morocco – Lulu, Milan – Lulu, and Monroe – Lulu 345 kV circuits. This alternative would sectionalize the path between Monroe and Allen Jct. Even if the circuit from Monroe to Lulu is lost, there still remains a 345 kV path between from ITCT to FE’s Allen Jct. The sag limit on the 636 ACSR from the Whiting – Custer 120 kV circuit would still need to be fully remediated up to the conductor rating. While this potential solution was found to remove the overloads on the Whiting – Custer 120 kV circuit, it is not the best long term solution because during the double circuit tower outage of the Monroe – Lulu and Monroe – Lalendorf (Y1-069), the 636 ACSR conductor from the Whiting – Custer 120 kV circuit is loaded up to 94%. Furthermore, once the Custer – Monroe 120 kV rebuild project is completed, the impedance of the path from Monroe to Whiting will be reduced, and the conductor from the Whiting – Custer 120 kV circuit will be loaded at 98% during this double circuit tower outage. Proposal 3: Mortar Creek 345 kV Station Install a new 345 kV switching Station (Mortar Creek) and cut in the Lemoyne – Majestic, Morocco – Milan – Monroe, and Monroe – Wayne 345 kV circuits. The sag limit on the 636 ACSR from the Whiting – Custer 120 kV circuit would still need to be fully remediated up to the conductor rating. While this potential solution was found to remove the overloads on the Custer – Whiting 120 kV circuit, it is not the best long term solution because during the N-1-1 contingency scenario involving the loss of both Monroe – Mortar Creek 345 kV circuits, the 636 ACSR conductor from the Custer – Whiting 120 kV circuit is loaded up to 93%. Furthermore, once the Custer – Monroe 120 kV rebuild project is completed, the impedance of the path from Monroe to Whiting will be reduced, and the conductor from the Custer – Whiting 120 kV circuit will be loaded at 97% during this contingency. | MI | MI | Proposed | BaseRel |  |  | 120 | 0 | 0 | 9.13 | 4 |  | METC_15_021 | METC | Bottom-Up | Submitted for Recommendation
2809 | 2015-10-02 | A in MTEP16 | B>A | East | METC | Garfield Avenue – Hemphill 138 kV Rebuild | Rebuild a ~9.5 mile-long portion of 336 ACSR conductor utilizing 1431 ACSR conductor on double-circuit, 138 kV structures, relocate a portion of the Weadock – Hemphill 138 kV line to the other side of the new structures. | 2019-12-31 | 2019-12-31 | 11000000 | The Garfield Avenue – Hemphill 138 kV line is projected to become overloaded for the shutdown plus contingency and double-circuit tower outage scenarios involving the Thetford - Hemphill 138 kV line and either the Delaney – Hemphill 138 kV or Thetford – Delaney 138 kV line. The overloads were identified in the shoulder peak, one Ludington pumping and 85% peak, six Ludington generating cases with flow to ITCT across the Michigan-Ontario interface. | 2019-12-31 |  | MI | MI | Proposed | BaseRel | Excluded |  | 138 | 0 | 0 | 9.5 | 1 | Y | 87 | METC | Bottom-Up | Submitted for Recommendation
3133 | 2015-09-15 | A in MTEP16 | B>A | East | METC | Bell Road - Cornell 138 kV Rebuild | Rebuild a ~4.3 mile-long portion of the Claremont – Cornell 2 line between Bell Road and Cornell. | 2019-12-31 | 2019-12-31 | 4350000 | The Bell Road – Cornell 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving either the Cornell – Goss 138 kV or Claremont – Cornell 1 138 kV line plus another facility. The overloads were identified in every model except for the 85% peak, six Ludington units generating and 70% peak, six Ludington units pumping cases with flow to IESO across the Michigan-Ontario interface. | 2019-12-31 |  | MI | MI | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 4.3 | 1 | Y | METC_15_022 | METC | Bottom-Up | Submitted for Recommendation
9422 | 2016-05-10 | A in MTEP16 |  | East | METC | Coldwater Interconnection | METC would construct a 138 kV, 4-breaker substations configured into a ring bus (Newton), and build a 3 mile. 138 kV, single circuit, line on new right-of-way between Michigan Ave and Newton substations. | 2017-04-01 | 2017-04-30 | 11090000 | Accomodate an interconnection request from the City of Coldwater. | 2017-04-01 |  | MI | MI | M3_Long Lead Materials | Other |  | Reliability | 138 | 0 | 3 | 0 | 2 |  | METC_15_017 | METC | Bottom-Up | Submitted for Recommendation
9695 | 2015-09-10 | A in MTEP16 |  | East | METC | Bullock 138 kV Terminal Equipment Upgrade (Dow Corning Line) | Upgrade terminal equipment at Bullock on the Dow Corning 138 kV line | 2018-12-31 | 2018-12-31 | 300000 | Terminal equipment at Bullock on the Bullock – Discovery Way Tap 138 kV section of the Bullock – Dow Corning 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Bullock – Tittabawassee 138 kV line and either the Redstone – Regal 138 kV or Gallagher – Tittabawassee 345 kV line. The overloads were identified in the shoulder peak, one Ludington pumping case with flow to ITCT across the Michigan-Ontario interface | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | METC_15_028 | METC | Bottom-Up | Submitted for Recommendation
9705 | 2015-09-10 | A in MTEP16 |  | East | METC | Alma - Regal #2 138 kV Sag Remediation | Remediate the sag limit on the Alma – Regal 2 138 kV line to a minimum of 208 MVA / 871 Amps | 2018-12-31 | 2018-12-31 | 200000 | The Alma - Regal 2 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Alma – Regal 1 138 kV line and either the Regal – Begole 138 kV, Nelson Rd – Vergennes 345 kV, or Livingston – Gallagher 345 kV line. The overloads were identified in the shoulder peak, one Ludington pumping case with flow to ITCT across the Michigan-Ontario interface. | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | METC_15_024 | METC | Bottom-Up | Submitted for Recommendation
9876 | 2015-10-14 | A in MTEP16 |  | East | METC | Karn - Manning 138 kV Sag Remediation | Remediate the sag limit on the Karn - Manning 138 kV line to a minimum of 396 MVA / 1657 Amps and upgrade terminal equipment at Karn | 2018-12-31 | 2018-12-31 | 620000 | The Karn - Manning 138 kV line is projected to become overloaded for the shutdown plus contingency involving the Karn – Saginaw River 138 kV and Atlanta – Karn – Thetford 138 kV lines. The overloads were identified in every model except for the shoulder peak, one Ludington unit pumping case with flow to ITCT across the Michigan-Ontario interface | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 2 |  | METC_15_027 | METC | Bottom-Up | Submitted for Recommendation
9880 | 2015-09-14 | A in MTEP16 |  | East | METC | Claremont - Manning #1 138 kV Sag Remediation | Remediate the sag limit on the Portsmouth Tap – Manning 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 378 MVA / 1581 Amps, remediate the sag limit on the Claremont – Portsmouth Tap 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 362 MVA / 1514 Amps, and upgrade terminal equipment at Claremont | 2018-12-31 | 2018-12-31 | 330000 | The Claremont - Manning 1 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Karn – Saginaw River 138 kV and Claremont – Manning 2 138 kV lines. The overloads were identified in the shoulder peak, one Ludington pumping case with flow to ITCT across the Michigan-Ontario interface. | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 2 |  | METC_15_025 | METC | Bottom-Up | Submitted for Recommendation
9881 | 2015-09-14 | A in MTEP16 |  | East | METC | Claremont - Manning #2 138 kV Sag Remediation | Remediate the sag limit on the Claremont – Manning 2 138 kV line to a minimum of 369 MVA / 1544 Amps and upgrade terminal equipment at Claremont | 2018-12-31 | 2018-12-31 | 1400000 | The Claremont - Manning 2 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Claremont – Manning 1 138 kV line and either the Karn – Saginaw River 138 kV or Cornell - Goss 138 kV line. The overloads were identified in the shoulder peak, one Ludington pumping case with flow to ITCT across the Michigan-Ontario interface. | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 2 |  | METC_15_026 | METC | Bottom-Up | Submitted for Recommendation
9929 | 2015-09-15 | A in MTEP16 |  | East | METC | Donaldson Creek - Pere Marquette 138 kV | Build new ~21 mile circuit from Donaldson Creek to Pere Marquette using 954 ACSR and OPGW. Replace equipment at Donaldson Creek, Pere Marquette, and White Lake Stations | 2019-12-31 | 2019-12-31 | 8700000 | Multiple stations near Amber, Donaldson Creek, Hart-88th Ave, Redwood, and White Lake Substations are projected to experience low voltage during contingency scenarios that disconnect two strong reactive power sources into the area, Lake Winds Generation and Amber – Pere Marquette 138 kV. These elements provide the aforementioned area with reactive power support from the north. The loss of these elements occurs during shutdown plus contingency events or protection failure at Amber. The violations were identified in the 2015 ITCTransmission/METC Near Term (2020) Assessment in the base study (50/50) at peak load and sensitivity study (70/30) at peak & off peak load levels. Multiple stations near Becker, Cobb, Latimer, Donaldson Creek, Stedman, and White Lake are projected to experience low voltage during a double circuit tower outage of BC Cobb - Tallmadge 1 & 2 138 kV. These lines provide the aforementioned area with reactive power support from the south. The overloads were identified in the 2015 ITCTransmission/METC Near Term (2020) Assessment in both peak load level models. | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 3 |  | METC_15_29 | METC | Bottom-Up | Submitted for Recommendation
9932 | 2015-09-15 | A in MTEP16 |  | East | METC | Karn - Saginaw River 138 kV Line Rebuild | Rebuild a ~2.7 mile-long portion of six-wired 3/0 copper conductor utilizing 1431 ACSR conductor on single-circuit, 138 kV structures, remediate the sag limit on the existing 1431 ACSR conductor to a minimum of 412 MVA / 1724 Amps, and upgrade terminal equipment at both Karn and Saginaw River stations | 2019-12-31 | 2019-12-31 | 8500000 | The Karn - Saginaw River 138 kV line is projected to become overloaded for several shutdown plus contingency scenarios involving the Karn – Manning 138 kV line and either the Atlanta – Karn – Thetford 138 kV, Iosco – Karn 138 kV, or the Karn – Garfield Avenue 138 kV line. The overloads were identified in every model for the shutdown plus contingency combination involving the Karn – Manning 138 kV and Atlanta – Karn – Thetford 138 kV lines and in both the 70% and 40% peak load level models with flow to ITCT across the Michigan-Ontario interface for the other shutdown plus contingency scenarios | 2019-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 16 | 4 |  | METC_14_026 | METC | Bottom-Up | Submitted for Recommendation
9945 | 2015-09-15 | A in MTEP16 |  | East | METC | 2017 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | 2017-12-31 | 2017-12-31 | 54276000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Condition | 345 | 138 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9956 | 2015-09-15 | A in MTEP16 |  | East | METC | 2018 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs | 2018-12-31 | 2018-12-31 | 49398000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Condition | 345 | 138 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9959 | 2016-03-23 | A in MTEP16 |  | East | METC | METC Customer Interconnections - Year 2019 | Customer interconnection requests and retirements. | 2017-12-31 | 2017-12-31 | 2500000 | Customer interconnection requests and retirements. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9960 | 2015-09-15 | A in MTEP16 |  | East | METC | 2019 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | 2019-12-31 | 2019-12-31 | 49398000 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Condition | 345 | 138 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9972 | 2016-06-16 | A in MTEP16 |  | East | METC | METC Four Mile Control Relocation Project | Replace METC relaying and controls at Four Mile Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | 2017-12-31 | 2017-12-31 | 3520000 | The many small Four Mile control buildings have maintenance, safety, and human performance concerns due to the buildings’ age and space constraints. Most of METC’s relaying and controls require high operations and maintenance expenses due to their age. The protection panels being dispersed into many small control buildings creates human performance issues with small workspace and difficult lighting. Additionally, lack of available panel space creates difficulty replacing relaying without extended shutdowns. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Relocation | 138 | 0 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9975 | 2016-06-16 | A in MTEP16 |  | East | METC | METC Verona Control Relocation | Replace METC relaying and controls at Verona Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | 2017-12-31 | 2017-12-31 | 2940000 | The many small Verona control buildings have maintenance, safety, and human performance concerns due to the buildings’ age and space constraints. Most of METC’s relaying and controls require high operations and maintenance expenses due to their age. The protection panels being dispersed into many small control buildings creates human performance issues with small workspace and difficult lighting. Additionally, lack of available panel space creates difficulty replacing relaying without extended shutdowns | 2017-12-31 |  | MI | MI | Proposed | Other |  | Relocation | 138 | 0 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9978 | 2015-09-15 | A in MTEP16 |  | East | METC | Eureka 138 kV Breaker Replacement | Replace the Eureka 138 kV circuit switcher 256 with a synchronous breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. | 2018-06-30 | 2018-06-30 | 510000 | The 2015 ITCT and METC short circuit analysis demonstrates that the Eureka 138 kV breaker is at risk of having to interrupt faults as high as 130% of its capability | 2018-06-30 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
9984 | 2015-09-15 | A in MTEP16 |  | East | METC | Tittabawassee 345 kV Breaker 38H9 Replacement | The proposed solution is to replace the Tittabawassee 345 kV breaker 38H9 with a breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. | 2018-06-30 | 2018-06-30 | 790000 | The 2015 ITCT and METC short circuit analysis demonstrates that the Tittabawassee 345 kV breaker 38H9 is at risk of having to interrupt faults as high as 149% of its capability. | 2018-06-30 |  | MI | MI | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  |  | METC | Bottom-Up | Submitted for Recommendation
10286 | 2015-10-30 | A in MTEP16 |  | East | METC | Campbell 138 kV Remove Circuit Breaker 588 Sparing Capability | Remove the Campbell 508 disconnect switch. Modify the relaying to remove 588 breaker sparing capability. | 2017-12-31 | 2017-12-31 | 88000 | The transient and dynamic stability analysis has identified possible dynamic instability for Campbell generation at Campbell 138 kV and some generators at nearby JD Young and Industry power plants for the fault scenarios of applying a 3-phase to ground fault at Tyler side of Campbell to Tyler 138 kV line CKT 1 when sparing Campbell 138 kV 588 breaker and cutting out the dual pilot relay schemes on the Campbell-Tyler 138 kV line. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  | METC_12_001 | METC | Bottom-Up | Submitted for Recommendation
10323 | 2016-05-12 | A in MTEP16 |  | East | METC | Coldwater Phase 2 Alternative 1 | Install a new 138 kV, 3 breaker substation (tentatively named Wagner) in a ring bus configuration in Union City, MI. Loop the existing 138 kV Alder Creek-Batavia line into Wagner, and modify relaying at Batavia to accommodate the new substation. Construct an approx. 13 mile, 138 kV line between Wagner and Newton on 138 kV, future double circuit, steel poles. | 2018-05-31 | 2018-05-31 | 39962000 | Accommodate an interconnection request from the City of Coldwater to provide a 2nd feed to the new Newton substation. | 2018-05-31 | This project is phase 2 of the MTEP16 project# 9422, and an alternative to MTEP16 project #11183. | MI | MI | Planned | Other |  | Distribution | 138 | 0 | 13.2 | 0 | 7 |  |  | METC | Bottom-Up | Submitted for Recommendation
10384 | 2015-11-23 | A in MTEP16 |  | East | METC | Verona - Barnum Creek Jct. 138 kV Sag Remediation | Fully remediate the sag limit on the 266.8 ACSR conductor from the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit to the conductor rating of 730 Amps / 174 VMVA (summer emergency) using new future double circuit (FDC) structures capable of supporting 954 ACSR in order to facilitate a rebuild of this circuit in the near future. | 2017-06-01 | 2017-06-01 | 1070000 | The Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit was projected to overload in the 2016 and 2019 models from the Attachment Y study performed by MISO for the Endicott (Project 1) Generator. The overloads on this branch are projected to occur during various contingencies including breaker open, segment, protection system failure, and N-1-1 contingencies. Many of the overloads on this branch are also projected to occur during contingencies involving breaker failure scenarios at the Morrow 138 kV station. | 2017-06-01 |  | MI | MI | M3_Long Lead Materials | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | METC_15_018 | METC | Bottom-Up | Submitted for Recommendation
10743 | 2016-02-11 | A in MTEP16 |  | East | METC | Covert Gen Interconnection (PJM-T94) | Phase 1 to construct a new control house at Palisades substation and replace the relaying associated with positions RH25 and FH27. Install OPGW on the new Palisades-Segreto #1 345 kV line and remove the METC SCADA equipment at Covert. | 2015-09-30 | 2015-09-30 | 3605000 | The existing Covert Plant has submitted an Interconnection Request to PJM to move from the METC footprint to ITCI in the PJM service territory. | 2015-09-30 |  | MI | MI | M5_In Service | GIP | Shared |  | 345 | 0 | 0 | 1.5 | 3 |  |  | METC | Externally Driven | Recommended
10744 | 2016-02-11 | A in MTEP16 |  | East | METC | J392 Generation Interconnection | Wolverine will construct the Stand Alone Network Upgrades which include the new 4 row, 11 breaker, 138 kV Van Tyle substation, laid out in a breaker and a half design. Ownership of these upgrades will be transferred to METC upon completion of the construction. METC will loop the 138 kV Livingston-Stover line into Van Tyle, and rebuild the new Livingston-Van Tyle line to double circuit structures, with OPGW being added to the new poles. 1431 ACSR conductor will be installed on both sides of the new structures to create Livingston-Van Tyle #1 and #2. A duel pilot relaying scheme will be installed on the Livingston-Emmett 138 kV line, and the Livingston substation will be expanded to include 2 new rows, and 5 additional breakers, on the 138 kV breaker and a half sub. Relaying upgrades will also occur at Gaylord. | 2016-05-06 | 2016-06-11 | 17702200 | The J392 generation interconnection was studied in the MI-Feb15 DPP cycle. This project represents the METC owned Network Upgrades required to interconnect the new gas plant to the METC system. | 2016-05-31 |  | MI | MI | M5_In Service | GIP | Shared |  | 138 | 0 | 0.2 | 8.4 | 5 |  |  | METC | Externally Driven | Recommended
11183 | 2016-05-12 | A in MTEP16 |  | East | METC | Coldwater Phase 2 Alternative 2 | This project would construct the new 138 kV, 3 breaker Chicago substation fed by looping the existing Coldwater-Project 1 138 kV circuit into Chicago. METC would also construct an approx. 5.5 mile, 138 kV, single circuit, line between Newton and Chicago substations on new ROW. | 2018-05-01 | 2018-05-31 | 21401000 | Accommodate a load interconnection request from the City of Coldwater for a new substation to feed a large industrial customer. This substation (Newton) would be fed from redundant, independent 138 kV lines from Michigan Ave and Chicago substations. | 2018-05-31 | This project is phase 2 of the MTEP16 project# 9422, and an alternative to MTEP16 project #10323. | MI | MI | Planned | Other |  | Distribution | 138 | 0 | 5.7 | 0 | 5 |  |  | METC | Bottom-Up | Submitted for Recommendation
11243 | 2016-05-13 | A in MTEP16 |  | East | METC | Verona - Barnum Creek Jct. 138 kV Rebuild | Rebuild the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit using 954 ACSR and OGPW on new 230 kV future double circuit structures. Replace PTS 3186. Upgrade terminal equipment at the Verona station. Also reconductor approximately 0.6 miles of the Verona – Foundry 138 kV circuit where it shares common structures with the Verona – Batavia 138 kV circuit. | 2018-05-31 | 2018-05-31 | 13300000 | The Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit is projected to overload during various contingencies including breaker open, segment, protection system failure, and N-1-1 contingencies. Many of the overloads on this branch are also projected to occur during contingencies involving breaker failure scenarios at the Morrow 138 kV station. The overloads on this branch are aggravated by the load increase from the Coldwater Interconnection (MTEP Project 9422) and the retirement of the Endicott (Project 1) Generator. | 2018-05-31 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 6.8 | 2 |  | METC_15_019 | METC | Bottom-Up | Submitted for Recommendation
11323 | 2016-06-06 | A in MTEP16 |  | East | METC | Newton 18 Mvar Capacitor | Add an 138kV 18 MVAR capacitor bank at the Newton 138kV station. | 2018-06-01 | 2018-06-01 | 0 | Newton sub and the surrounding area can experience low voltages for the outage of Batavia Coldwater, either by itself or in combination with other 138kV line outages. The issue will become worse as new load is added to the Coldwater system. | 2018-06-01 |  | MI | MI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | METC-16-028 | METC | Bottom-Up | Submitted for Recommendation
4385 | 2015-11-23 | A in MTEP16 | B>A | East | WPSC | Burnips to Fairview | Burnips to Fairview Rebuild | 2018-12-31 | 2018-12-31 | 3500000 | Loading on this line reaches 99% of it emergency limit in 2018 |  |  | MI | MI | Proposed | Other | Not Shared | Reliability | 69 | 0 | 0 | 11.6 | 2 | Y | BP-FV | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Recommendation
9899 | 2015-09-15 | A in MTEP16 |  | East | WPSC | Redwood to Scottville Rebuild | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | 2018-12-01 | 2018-12-31 | 10250000 | The single contingency loss of Pere Marquette to Amber and the category P2 contingency for the internal breaker fault of the Pere Marquette 7M9 and Amber 188 causes overloads on this line in the 2017 summer peak case identified in MTEP15. In addition, this line segment was being evaluated for a future rebuild based on condition. The line was built in 1967 and has 45% condemned or damaged structures. |  |  | MI | MI | Proposed | Other |  | Reliability | 69 | 0 | 0 | 20.59 | 4 |  | RW-SV Rebuild | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Recommendation
9913 | 2015-09-15 | A in MTEP16 |  | East | WPSC | 2017 Battery Bank Replacement Project | This project replaces battery banks and chargers that have reached the end of their useful life at transmission stations. | 2017-12-31 | 2017-12-31 | 70000 | Agining infrastrucure replacement. |  |  | MI | MI | Planned | Other |  | Condition | 69 | 0 | 0 | 0 | 1 |  | 2017 Battery Bank Replacement Project | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Recommendation
9915 | 2015-09-15 | A in MTEP16 |  | East | WPSC | Oden Relay Upgrade | Upgrade the relaying on the Oden-Emmet terminal | 2017-12-31 | 2017-12-31 | 35000 | The current communication assisted trip scheme on the Oden - Emmet line is outdated and the telephone line is not being maintained well by the phone company. This scheme will install line differential relaying with a fiber interface. ITC plans to install OPGW on the Oden - Emmet line and Consumers will install similar relaying at Emmet to accomidate this protection upgrade. |  |  | MI | MI | Proposed | Other |  | Condition | 69 | 0 | 0 | 0 | 1 |  | OE Relay Upgrade | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Recommendation
11023 | 2016-04-11 | A in MTEP16 |  | East | WPSC | J392 Generator Interconnection | Upgrades determined in the FEB2015 DPP studies to connect J392. Wolverine to construct the following: -Advance 138kV station and 138/69kV transformer -Gaylord 138kV 4 breaker ring bus to accommodate 3rd line into the station (2016) -Gaylord 138kV 6 breaker ring bus and 2nd 138/69KV transformer (2018) -Upgrades to Elmira, Deer Lake and Alpine distribution subs from 69kV to 138kV operation -Conversion of existing Gaylord - Advance 69kV line to 138kV operation, new lines will be Gaylord - Van Tyle and Van Tyle to Advance -Rebuild of Gaylord - Livingston 138kV line to 795ACSS | 2016-04-30 | 2018-10-31 | 13980072 | Upgrades determined in the FEB2015 DPP studies required to connect J392. | 2016-05-31 |  | MI | MI | Under Construction | GIP | Not Shared |  | 138 | 13.09 | 1 | 23.78 | 8 |  |  | Wolverine Power Supply Cooperative, Inc. | Externally Driven | Recommended
9662 | 2015-10-13 | A in MTEP16 |  | South | AECC | Harrison South Transformer Upgrade | Upgrade the autotransformer at the Harrison South 161/69 kV substation. The four single phase 5.6 MVA, 161/69 kV transformers will be replaced with the three phase 27.5 MVA, 161/69 kV autotransformer from the Black Rock 161/69 kV substation. | 2017-01-01 | 2017-01-01 | 600000 | The upgrade is needed due to normal load growth. | 2017-01-01 |  | AR | AR | Planned | Other |  | Distribution | 161 | 0 | 0 | 0 | 1 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
9663 | 2015-10-13 | A in MTEP16 |  | South | AECC | Tap EAI Newport - Balch 161 kV line: Construct South Newport 161/13.2 kV substation | Construct 20 MVA, 161/13.2 kV substation under EAI Newport - Parkin 161 kV line. The load for this substation will be transferred from the Newport and Cherokee Acres distribution delivery points. Once the load is transferred the two distribution delivery points will no longer be needed. Edit: POD/substation name will likely be changed from South Newport to Newport East. | 2017-07-01 | 2017-07-01 | 500000 | The substation is needed to improve reliability to the Farmers Electric system by replacing two distribution delivery points. | 2017-07-01 | Proposed property location: 35°36'25.20"N, 91°14'01.97"W Alternate property location: 35°36'26.53"N, 91°14'34.73"W Please note the alternate location is not on the same transmission line. It is on the Entergy Newport to Bailey 161 kV transmission line. | AR | AR | Planned | Other |  | Distribution | 161 | 13.2 | 0 | 0 | 1 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
10204 | 2016-05-06 | A in MTEP16 |  | South | AECC | Tap EAI Moses to Bailey 161kV line, Construct 161/13.2kV Hunter North substation | Tap EAI Moses to Bailey 161kV line, Construct 161/13.2kV Hunter North substation | 2018-06-01 | 2018-06-01 | 500000 | Build substation closer to load center and increase reliability | 2018-06-01 |  | AR | AR | Proposed | Other |  | Reliability | 161 | 0 | 0 | 0 | 1 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
10205 | 2015-11-12 | A in MTEP16 |  | South | AECC | Bee Branch to Damascus 161kV transmission line, 161/13.2kV substation | Build 6.8 mile 161kV line from the existing AECC Bee Branch substation to the proposed Damascus substation, add 161kV line breaker, build 161/13.2kV Damascus substation. | 2017-02-28 | 2017-02-28 | 8000000 | Increase reliability by building station closer to load center | 2017-02-28 |  | AR | AR | Proposed | Other |  | Distribution | 161 | 0 | 0 | 0 | 3 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
10206 | 2016-05-06 | A in MTEP16 |  | South | AECC | Clinton West to Partain 161kV line, 161/69kV Partain substation | Build 5 position ring bus at the AECC Clinton West substation, Build 14 mile 161kV line from the existing Clinton West substation to the proposed Partain substation, Build 3 position ring bus at the proposed Partain substation, Build the proposed Partian 161/69kV substation. | 2020-12-01 | 2020-12-01 | 27000000 | Provide voltage support and increase reliability to existing Clinton West and Heber Springs North 69kV systems. Will also increase reliability on the EAI Hill Top to Quitman 161kV line. | 2020-12-01 |  | AR | AR | Proposed | Other |  | Reliability | 161 | 69 | 0 | 0 | 3 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
10207 | 2015-10-12 | A in MTEP16 |  | South | AECC | 5 position ring bus at Heber Springs North, 26 mile 161kV line form Heber Springs North to Partain | Build 5 position ring bus at the existing AECC Heber Springs North, build 26 mile 161kV line from the existing Heber Springs North substation to the proposed Partain 161/69kV substation | 2021-06-01 | 2021-06-01 | 23000000 | Increase reliability at the proposed Partian substation and on the Heber Springs North 69kV system. | 2021-06-01 |  | AR | AR | Proposed | Other |  | Reliability | 161 | 0 | 0 | 0 | 2 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Recommendation
10122 | 2015-10-15 | A in MTEP16 |  | South | AXLA | Hunter - Downtown 138 kV Reconductor | Reconductor the existing Hunter - Downtown 138kV transmission line | 2017-06-01 | 2017-06-01 | 340000 | To alleviate reliability issues and improve capacity transfer | 2016-07-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 | Y | AXLA PRJ_01_MTEP16 | City Of Alexandria | Bottom-Up | Submitted for Recommendation
10123 | 2015-10-15 | A in MTEP16 |  | South | AXLA | Prescott - Sterkx 138 kV Recondutor | Reconductor the existing Prescott - Sterkx 138kV transmission line | 2017-06-01 | 2017-06-01 | 490000 | To alleviate reliability issues and improve capacity transfer | 2016-07-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 | Y | AXLA PRJ_02_MTEP16 | City Of Alexandria | Bottom-Up | Submitted for Recommendation
9542 | 2015-09-11 | A in MTEP16 |  | South | CLECO | Dolet Hills Mine Line Tap | Tap the existing 230 kV line from Dolet Hills to Mansfield Compressor to serve existing load which is moving its operations. | 2016-12-01 | 2016-12-01 | 5000000 | Dolet Hill Mine is moving its operation. Studies were conducted to see if they could run their motors and drag lines from the existing 69 kV system if it was extended to the new location. It was determined that it would be better to serve this load from the 230 kV system instead extending the radial 69 kV system. | 2016-12-01 |  | LA | LA | Proposed | Other |  | Reliability | 230 | 0 | 0 | 0 | 1 |  | 19944 | Cleco Power LLC | Bottom-Up | Submitted for Recommendation
9713 | 2015-09-11 | A in MTEP16 |  | South | CLECO | Dolet Hills Breaker Replacements | Replace one of the 345 kV Breakers at Dolet Hills due to aging equipment and trouble maintaining existing breakers. | 2016-11-01 | 2016-11-01 | 294580 | Parts for existing breakers are becoming harder and harder to come by due to their age. |  |  | LA | LA | Proposed | Other |  | Reliability | 345 | 0 | 0 | 0 | 1 |  |  | Cleco Power LLC | Bottom-Up | Submitted for Recommendation
9715 | 2015-09-11 | A in MTEP16 |  | South | CLECO | Wax Lake Cap Switcher Replacements | Replaces existing MOS 8374 & 8373 with Cap Switcher at Wax Lake | 2016-10-01 | 2016-10-01 | 406013 | Old MOS's have failed several times in the past and need to be replaced. | 2016-10-01 |  | LA | LA | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Cleco Power LLC | Bottom-Up | Submitted for Recommendation
10983 | 2016-04-04 | A in MTEP16 |  | South | CLECO | Hopkins Breaker Addition | Add a second Breaker in Series with Hopkins Breaker 8061. | 2017-05-01 | 2017-05-01 | 300000 | This Project eliminates the P2.4 contingency at Hopkins substation which was Identified in Cleco Annual Transmission Planning Assessment. | 2016-06-01 |  | LA | LA | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Cleco Power LLC | Bottom-Up | Submitted for Recommendation
4665 | 2015-09-28 | A in MTEP16 | B>A | South | Entergy-AR | Mabelvale: Replace 500-115 Autos | Upgrade both Mabelvale 500/115 kV autotransformers to 598MVA. | 2017-12-01 | 2017-12-01 | 17417000 | Loss of either of the existing Mabelvale 500/115 kV autotransformers results in thermal overload of the other. Also multiple EHV breaker failures in the Mabelvale substation resulting in 500 kV lines + autos results in auto overloading. | 2020-06-01 | None | AR | AR | Proposed | BaseRel |  |  | 500 | 115 | 0 | 0 | 2 | Y | 12-EAI-019 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
7942 | 2015-09-09 | A in MTEP16 | B>A | South | Entergy-AR | Mayflower - Morgan: Rebuild 15kV line | Mayflower - Morgan: Rebuild 115kV line | 2019-06-01 | 2019-06-01 | 4877301 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of Keo-White Bluff & Keo-Wrightsville 500kV lines (P2-3, EHV Breaker Failure) causes overload of Mayflower - Morgan Rebuild 5 miles of 115kV line | 2019-06-01 | Build new 23 mile 500kV line from Mayflower to Holland Bottom | AR | AR | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 5 | 1 |  | 15-EAI-004 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
7944 | 2015-09-16 | A in MTEP16 | B>A | South | Entergy-AR | Stuttgart Ricuskey - Stuttgart Ind: Rebuild 115kV line | Stuttgart Ricuskey - Stuttgart Ind: Upgrade 115kV line to 176MVA | 2018-01-30 | 2018-01-30 | 2526158 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of Keo-White Bluff & Keo-Wrightsville 500kV lines (P2-3, EHV Breaker Failure) causes overload of Stuttgart Ricuskey - Stuttgart Ind. Need accelerated from 6/1/2024 to 1/30/2018 base on J348 GIA confirmation. | 2018-01-30 | 1) Build new 23 mile 500kV line from Mayflower to Holland Bottom or 2) Build new 6 mile 115kV line from Stuttgart North to Stuttgart Industrial, add breakers at Stuttgart North Switching Station and Stuttgart Industrial | AR | AR | Conceptual | GIP | Not Shared |  | 115 | 0 | 0 | 2.6 | 1 |  | 15-EAI-007 | Entergy Arkansas | Externally Driven | Recommended
9673 | 2015-09-09 | A in MTEP16 |  | South | Entergy-AR | El Dorado Install 2nd 500/115 Autotransformer | Install 2nd-598MVA 500/115 kV autotransformer at El Dorado EHV. | 2018-06-01 | 2018-06-01 | 16446045 | Loss of McNeil 500/115 kV autotransformer, loss of Mt Olive - El Dorado 500 kV line, loss of McNeil 500 kV breaker B4612, B4515, B4618 result in thermal overload of existing El Dorado 500/115 kV auto | 2016-06-01 |  | AR | AR | Proposed | BaseRel |  |  | 500 | 115 | 0 | 0 | 1 |  | 16-EAI-002 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9691 | 2015-09-24 | A in MTEP16 |  | South | Entergy-AR | Lonoke East 115kV: 20.5MVAR Capacitor Bank | Install new 20.5 MVAR Capacitor bank on Lonoke East 115 kV. | 2017-06-01 | 2017-06-01 | 1456861 | Loss of Lynch - NLR Galloway results at low voltages at Carlisle and Lonoke East 115 kV substations. | 2017-06-01 |  | AR | AR | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-009 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9693 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Pleasant Hill: Add tertiary reactors | Add three 30 MVAR reactors on the tertiary windings of the 500/161/13.8 kV transformer at the Pleasant Hill EHV substation to maintain the voltages within the limits defined in the Entergy Local Planning Criteria. | 2017-10-01 | 2017-10-01 | 2184660 | The transmission network in the Pleasant Hill area experiences high voltages during light loading conditions. Transmission Operations has confirmed high voltage issues in this area as well, and requested voltage control devices be installed at Pleasant Hill. | 2017-10-01 |  | AR | AR | Conceptual | BaseRel |  |  | 500 | 161 | 0 | 0 | 1 |  | 16-EAI-014 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9696 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Newport 161 kv: Address Newport Flicker Issues | Build a 4-breaker switching station near Newport Industrial and re-terminate the Newport-Swifton 161 kV line into the new switching station. Build a new 161 kV line between the Newport switching station and Newport Industrial to eliminate the voltage issue | 2018-06-01 | 2018-06-01 | 15150000 | The loss of the Newport-Newport Industrial 161 kV line could potentially cause flicker issues around the Newport area. The issue is heightened during times of reduced generation near the area. | 2018-06-01 |  | AR | AR | Conceptual | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  | 16-AI-017 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9697 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Trumann-Trumann West: Upgrade existing 161kV line | Re-build 6.5 mile long line to a minimum rating of 1300A. | 2018-06-01 | 2018-06-01 | 12115000 | The Trumann-Trumann West 161 kV line overloads in 2018 Summer for the loss of the Sans Souci – Driver 500 kV line | 2018-06-01 |  | AR | AR | Conceptual | BaseRel |  |  | 161 | 0 | 0 | 6.5 | 1 |  | 16-EAI-001 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9698 | 2016-02-03 | A in MTEP16 |  | South | Entergy-AR | El Dorado East - El Dorado Jackson 115kV rebuild | Upgrade El Dorado East - El Dorado Jackson 115 kV line to minimum 1300A. | 2018-06-01 | 2018-06-01 | 4926295 | Loss of El Dorado EHV - El Dorado Donan 115 kV overloads the El Dorado East - El Dorado Jackson 115 kV. | 2018-06-01 |  | AR | AR | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 2.92 | 1 |  | 16-EAI-006 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9703 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Bono: New 161kV Substation | Build new 161kV substation to support load growth. | 2017-10-01 | 2017-10-01 | 9380200 | The nearby Greenbrier substation is a 2 transformer station with a 30 MVA and a 50 MVA transformer. There are no ties to Greenbrier that would allow transfer of load to another source. In the winter of 2015, The #1 transformer(30 MVA) was loaded at 30.24 MVA and the #2 transformer (50 MVA) was loaded at 27.35 MVA. There would be loss of load for the loss of either transformer at 2015 winter levels. The present growth rate is 2.5% . Therefore, total load at risk in 2017 is projected to be 27.51 MVA. This justifies the addition of a new 161kV substation. | 2017-10-01 | Upgrade existing #1 transformer from 30 MVA to 50 MVA. There would still be Load at Risk in 2015 and beyond if either of the two transformers fails. | AR | AR | Conceptual | Other |  | Distribution | 161 | 0 | 0 | 0 | 1 |  | 16-EAI-007 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9704 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | London North: New 161kV Substation | Construct new London North 161kV substation | 2017-10-01 | 2017-10-01 | 9244000 | The 8.4/10.5 MVA 161/13.8 KV London Substation Transformer was loaded near capacity in January 2014. The substation power factor is 97% . Annual area load growth is 2%. There are 2 feeder breakers in the station serving 530 customers including residential, commercial, Major Account Cargill and the Arkansas Nuclear One Plant(ANO). ANO added 300 KW of load in 2014 and the Nuclear Regulatory Commision is requiring Backup water supply that will require adding 2- 600 HP motors in 2017. The London Substation transformer is projected to be loaded at 110% in the winter of 2017. Therefore we are adding a new 161kV substation to support the load growth in the area. | 2017-10-01 |  | AR | AR | Conceptual | Other |  | Distribution | 161 | 0 | 0 | 0 | 1 |  | 16-EAI-008 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9707 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Camden Maguire115kV: Reconfigure station | Reconfigure Camden Maguire 115 kV substation so that a single bus failure will not open all the elements in the Camden Maguire substation. Some potential configurations are double bus double breaker, breaker and a half, and ring bus. The final configuration will be decided during project scoping. | 2017-06-01 | 2017-06-01 | 5772470 | The Camden Maguire 115 kV substation is configured as a single bus single breaker substation. A 115 kV bus fault will clear the bus and result in low voltages across the area 115 kV network per the Entergy Planning Criteria. | 2016-06-01 | No suitable alternatives identified. | AR | AR | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-011 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9708 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | ISES 161kV: Reconfigure station | Reconfigure the Independence 161 kV station to a breaker-and-a-half configuration or a double bus/double breaker configuration to help eliminate area thermal and voltage violations. | 2017-10-01 | 2017-10-01 | 9100851 | A fault at Independence 161 kV bus tie breaker results in loss of both the 161 kV operating buses at Independence. This causes low voltages along the 115 kV and 161 kV networks around Independence, AR. The bus tie breaker fault also results in thermal violations on the 115 kV network around Holland Bottoms. | 2016-06-01 | There were no suitable alternatives found. | AR | AR | Conceptual | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  | 16-EAI-004 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
9709 | 2015-09-10 | A in MTEP16 |  | South | Entergy-AR | Mabelvale 115kV: Reconfigure Station | Reconfigure the Mabelvale 115 kV substation so that a single bus tie breaker failure will not open all the elements in the Mabelvale 115 kV substation. Some potential configurations are double bus double breaker, breaker and a half, and ring bus. The final configuration will be decided during project scoping. | 2019-06-01 | 2019-06-01 | 17446076 | The Mabelvale 115 kV substation is configured as two separate single bus single breaker substations with a bus tie breaker connecting the two operating buses. A single internal breaker fault on the bus tie breaker will result in load shed event in the West Little Rock 115 kV network | 2016-06-01 | No suitable alternatives identified. | AR | AR | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-012 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
10044 | 2015-09-17 | A in MTEP16 |  | South | Entergy-AR | Goodwin Road 115 kV: New SS for GIA J348 | Construct a new 115 kV 3 breaker ring bus switching station named Goodwin Road on the Stuttgart Ricuskey - Almyra 115 kV line. | 2018-01-30 | 2018-01-30 | 10064000 | New generation interconnection point | 2018-01-30 |  | AR | AR | Proposed | GIP | Not Shared |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-018 | Entergy Arkansas | Externally Driven | Recommended
11483 | 2016-06-30 | A in MTEP16 |  | South | Entergy-AR | Benton Hurricane Lake 115 kV: New point-of-delivery | Cut-in new wholesale delivery point on River Ridge - Mabelvale 115 kV line | 2017-05-01 | 2017-05-01 | 1589494 | Local load growth | 2017-05-01 |  | AR | AR | Planned | Other |  | Reliability | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-023 | Entergy Arkansas | Bottom-Up | Submitted for Recommendation
4634 | 2015-09-11 | A in MTEP16 | B>A | South | Entergy-LA | Ninemile to Westwego 115 kV: Reconductor Line | Reconductor the existing Ninemile to Westwego115 kV line to achieve a minimum rating of320 MVA and upgrade terminal equipment at Ninemile and Westwego line bays to achieve the minimum rating of 320 MVA. | 2018-06-01 | 2018-06-01 | 9026000 | The existing Ninemile to Westwego 115 kV transmission line will thermally overload during the single contingency loss (P2-1) of the Ninemile to Harvey 2 115 kV transmission line. To alleviate this thermal constraint , it is proposed to rebuild the existing Ninemile to Westwego 115 kV line. This project will provide the thermal capacity needed due to address the single contingency event. | 2016-06-01 | None | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 5.65 | 2 | Y | 13-ELL-006 | Entergy | Bottom-Up | Submitted for Recommendation
4639 | 2015-09-13 | A in MTEP16 | B>A | South | Entergy-LA | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements | Reconductor the existing Ninemile to Harvey2 115 kV line to achieve a minimum rating of320 MVA and upgrade terminal equipment at Ninemile and Harvey2 line bays to achieve the minimum rating of 320 MVA. | 2018-06-01 | 2018-06-01 | 15121000 | The existing Ninemile to Harvey2 115 kV transmission line will thermally overload during the single contingency loss of the Ninemile to Westwego 115 kV transmission line (P1-2). To alleviate this thermal constraint, this project will upgrade the existing Ninemile to Harvey2 115 kV line in order to provide the thermal capacity required to eliminate the contingency overload. | 2016-06-01 | None | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 9.5 | 2 | Y | 14-ELL-006 | Entergy | Bottom-Up | Submitted for Recommendation
7949 | 2016-05-10 | A in MTEP16 | B>A | South | Entergy-LA | Solac 230-69 kV: Upgrade Both Autos | Replace both 230/69 kV AT with 300MVA | 2018-06-01 | 2018-06-01 | 8457000 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Each of the 138-69 kV Solac autotransformers will exceed their thermal rating during the single contingency (P1-3) transformer loss of one autotransformer on the other. This project will mitigate the thermal load violations on the two autotransformers by installing a third 138-69 kV Autotransformer at Solac." | 2023-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 230 | 69 | 0 | 0 | 2 |  | 15-EGL-010 | Entergy | Bottom-Up | Submitted for Recommendation
7950 | 2015-11-06 | A in MTEP16 | B>A | South | Entergy-LA | East Broad to Ford 69 kV line: Reconductor line | Re-conductor East Broad to Ford 69 kV line | 2018-06-01 | 2018-06-01 | 1474000 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The East Broad to Ford 69 kV line will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Contraband to Solac 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor." | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 1.49 | 1 |  | 15-EGL-011 | Entergy | Bottom-Up | Submitted for Recommendation
7952 | 2015-09-13 | A in MTEP16 | B>A | South | Entergy-LA | Contraband to Solac 69 kV line: Reconductor line | Re-conductor Contraband to Solac 69 kV line | 2018-06-01 | 2018-06-01 | 4125000 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Contraband to Solac 69 kV line will exceed its thermal rating during the single contingency (P2-1) open breaker at East Broad toward Ford 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor." | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 2.26 | 1 |  | 15-EGL-012 | Entergy | Bottom-Up | Submitted for Recommendation
9682 | 2015-09-10 | A in MTEP16 |  | South | Entergy-LA | Vienna - Trussell Crossing: Upgrade line | Upgrade the Vienna - Trussell Crossing 115 kV to a minimum of 260MVA. | 2020-06-01 | 2020-06-01 | 8823757 | The P1.2 loss of Sarepta - Minden 115 kV results in thermal overloading on the Vienna - Trussell Crossing 115 kV. | 2020-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 6.9 | 1 |  | 16-ELN-001 | Entergy | Bottom-Up | Submitted for Recommendation
9684 | 2015-11-06 | A in MTEP16 |  | South | Entergy-LA | Cadeville: New distribution substation | Construct a new 115 kV substation in the Cadeville area to serve area load | 2018-06-01 | 2018-06-01 | 41643000 | Area distribution load | 2018-06-01 |  | LA | LA | Proposed | Other |  | Distribution | 115 | 0 | 0 | 0 | 2 |  | 16-ELN-004 | Entergy | Bottom-Up | Submitted for Recommendation
9686 | 2015-09-10 | A in MTEP16 |  | South | Entergy-LA | Lake Providence: New distribution substation | Construct a new radial 115 kV transmission line to the Lake Providence area to serve area load. | 2020-06-01 | 2020-06-01 | 31830074 | Distribution has requested a new substation to serve area distribution load in East Carroll Parish. | 2020-06-01 |  | LA | LA | Proposed | Other |  | Distribution | 115 | 0 | 15 | 0 | 2 |  | 16-ELN-005 | Entergy | Bottom-Up | Submitted for Recommendation
9690 | 2015-09-10 | A in MTEP16 |  | South | Entergy-LA | Hodge: Replace existing substation | Construct a new 230 kV substation to serve area load in the Hodge area. | 2018-12-01 | 2018-12-01 | 14121450 | The existing Hodge substation needs to be relocated. The facility experiences extreme equipment degradation due to environmental conditions in the area. The facility will be relocated to the east and from the 115 kV system to the 230 kV system to improve area reliability. | 2018-12-01 |  | LA | LA | Proposed | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 |  | 16-ELN-010 | Entergy | Bottom-Up | Submitted for Recommendation
9763 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Baker to Blount 69kV: Reconductor Line | Upgrade the rating on the Baker to Blount 69 kV line. This includes recondutor and upgrading station equipment. | 2018-06-01 | 2018-06-01 | 5182000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Open breaker contingency at Port Hudson 69 kV causes a thermal violation on the Baker to Blount 69 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-004 | Entergy | Bottom-Up | Submitted for Recommendation
9765 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Harelson to Line 369 Tap 69 kV: Reconductor Line | Reconductor the Harelson to Line 369 Tap 69 kV line. | 2018-12-01 | 2018-12-01 | 3165000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Harelson to Gloria 69 kV causes a thermal violation on the Harelson to Line 369 Tap 69 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-006 | Entergy | Bottom-Up | Submitted for Recommendation
9770 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Goosport to L673 TP 69 kV: Upgrade Station Equipment | Upgrade the substation equipment at Goosport to increase the rating of the line. | 2016-11-18 | 2016-11-18 | 145205 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Goosport to L-673 TP 69 kV line section will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Lake Charles Bulk to Chlomal 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-011 | Entergy | Bottom-Up | Submitted for Recommendation
9771 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Construct Jefferson Davis 138/69 kV Substation | Construct new Jefferson Davis 138/69 kV substation. | 2019-06-01 | 2019-06-01 | 76570000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 69 | 0 | 0 | 1 |  | 16-EGL-012-1 | Entergy | Bottom-Up | Submitted for Recommendation
9772 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Colonial Welsh TP to Jefferson Davis 138 kV: Construct 138 kV line | Construct a new line from Colonial Welsh Tap to the new Jefferson Davis 138 kV station. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-012-2 | Entergy | Bottom-Up | Submitted for Recommendation
9773 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Jefferson Davis to Carter Construct 69 kV line | Build a new 69 kV line from Jefferson Davis to Carter substation | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-012-3 | Entergy | Bottom-Up | Submitted for Recommendation
9774 | 2016-03-11 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Jefferson Davis to Compton Construct 69 kV line | Construct 5 miles of double circuit 69 kV with a conductor rating of at least 880 A to a cut in point on 69 kV L-13 two miles south of the existing Compton 69 kV substation. Rebuild 2 miles of 69 kV L-13 from new cut in point to Compton with a conductor rating of at least 880 A. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-012-4 | Entergy | Bottom-Up | Submitted for Recommendation
9775 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Derouen 69 kV Cut into L-11 | Cut the Derouen 69 kV substation in and out of Line 11. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-012-5 | Entergy | Bottom-Up | Submitted for Recommendation
9776 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Lawtag 69 kV Cut into L-13 & Close NO @ L-13A | Cut line number 13 in and out of the Lawtag 69 kV substation. Also, close the normally open point on line number 13A. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-012-6 | Entergy | Bottom-Up | Submitted for Recommendation
9777 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Welsh 69 kV Cut into L-13A | Cut the Welsh 69 kV substation in and out of line 13A. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-012-7 | Entergy | Bottom-Up | Submitted for Recommendation
9778 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Colonial Welsh TP to Jefferson Davis 138 kV Reconductor | Reconductor the Colonial Welsh Tap to Jefferson Davis 138 kV line. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple P1-2 and P1-3 contingencies cause thermal overloads and low voltage on the 69 kV system in Lake Charles, LA. This project in conjunction with others mitigates the thermal overloads and low voltage. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-012-8 | Entergy | Bottom-Up | Submitted for Recommendation
9779 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 2: Carter to Serpent 69 kV Reconductor | Reconductor the Carter to Serpent 69 kV line. | 2018-12-01 | 2018-12-01 | 19235078 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Carter to Serpent 69 kV line section will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Compton to Elton 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2016-12-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-013 | Entergy | Bottom-Up | Submitted for Recommendation
9780 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 3: Compton to Elton 69 kV Reconductor | Reconductor Comton to Elton 69 kV line. | 2019-12-01 | 2019-12-01 | 12782000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Compton to Elton 69 kV line section will exceed its thermal rating during the single contingency (P2-1) open breaker at Carter (B27225). This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2017-12-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-014 | Entergy | Bottom-Up | Submitted for Recommendation
9782 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 4: Lake Arthur 69 kV Move NO Point | Move the normally open point at the Lake Arthur 69 kV substation. | 2022-06-01 | 2022-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P0 low voltage at Klondike and Lake Arthur 69 kV. Moving the normally open point to the Lake Arthur to Klondike section mitigates the low voltage issues. | 2018-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-016 | Entergy | Bottom-Up | Submitted for Recommendation
9786 | 2015-10-21 | A in MTEP16 |  | South | Entergy-LA | Nelson 138 kV: Add L-274 to Breaker-and-a-half Scheme | Add L-274, L-654, L-656 and L-698 to the double bus double breaker scheme at Nelson. | 2017-06-01 | 2017-06-01 | 1142000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Nelson to Mossville 138 kV L-656 overloads in 2016 Summer for a Nelson 138 kV breaker failure (P2-3). Low voltage at Lake Charles Bulk 138 kV for a Nelson 138 kV breaker failure (P2-3). The violations will be mitigated by adding L-274, L-654, L-656 and L-698 to the double bus double breaker scheme at Nelson. | 2016-06-01 |  | LA | LA | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-020 | Entergy | Bottom-Up | Submitted for Recommendation
9787 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Air Products to Giegy 138kV: Upgrade Substation Equipment | Upgrade substation equipment on the Air Products and Giegy terminals to increase the rating of the line. | 2016-06-01 | 2016-06-01 | 300000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Willow Glen to Alchem 138 kV line causes a thermal violation on the Air Products to Geigy 138 kV line. This project will alleviate the thermal violation by upgrading station equipment. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-021 | Entergy | Bottom-Up | Submitted for Recommendation
9788 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Port Barre 69 kV: Install Cap Bank | Install a capacitor bank at the Port Barre substation. | 2018-06-01 | 2018-06-01 | 786000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The loss of Champagne AT 1 or AT 2 clears the entire 138 kV bus at Champagne. This P1-3 contingency causes low voltage on the 69 kV stations out of Champagne including Champagne, Port Barre, Gulf Krotz. Install an 11 MVar Capacitor bank on the 69 kV at Port Barre. Champagne could be an alternative site. This option also currently alleviates the bus fault contingency at Champagne. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-022 | Entergy | Bottom-Up | Submitted for Recommendation
9790 | 2015-12-03 | A in MTEP16 |  | South | Entergy-LA | Swisco 138 kV: Construct New Substation | Construct a new substation to serve area load. | 2017-06-01 | 2017-06-01 | 8191000 | Distribution System Load Growth This distribution project is needed to relieve distribution facility loadings in the Carlyss area and provide service to a rapidly developing commercial and residential area. | 2017-06-01 |  | LA | LA | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-026 | Entergy | Bottom-Up | Submitted for Recommendation
9791 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Thompson Road 230 kV: Construct New Substation | Construct a new substation to serve area load. | 2018-06-01 | 2018-06-01 | 9252000 | Distribution System Load Growth This distribution project is needed to relieve distribution facility loadings in the Carlyss area and provide service to a rapidly developing commercial and residential area. | 2018-06-01 |  | LA | LA | Proposed | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-027 | Entergy | Bottom-Up | Submitted for Recommendation
9792 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Lowe Grout Road 138 kV: Construct New Substation | Construct a new substation to serve area load. | 2019-06-01 | 2019-06-01 | 6989000 | Distribution System Load Growth This distribution project is needed to relieve distribution facility loadings in the Iowa, LA area and provide service to a rapidly developing commercial and residential area. | 2019-06-01 |  | LA | LA | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-028 | Entergy | Bottom-Up | Submitted for Recommendation
9794 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Repapco to Port Hudson Station 230 kV: Upgrade Substation Equipment | Upgrade substation equipment at on the Repapco to Port Hudson 230 kV line. | 2018-06-01 | 2018-06-01 | 101000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. For the loss of the Fancy to Horseshoe 230 kV line along with the Repapco Cogen the Port Hudson to Repapco 138 kV line overloads in 2018S | 2018-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-032 | Entergy | Bottom-Up | Submitted for Recommendation
9795 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Nesser 69 kV: New Cap Bank | Add a capacitor bank to the Nesser 69 kV substation. | 2017-12-01 | 2017-12-01 | 1053000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The loss of the Harelson to Line 372 Tap 69 kV line creates voltage violations at Nesser and Jones Creek 69 kV stations in 2017S. | 2017-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-033 | Entergy | Bottom-Up | Submitted for Recommendation
9801 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | North Norco 115 kV: Add Cap Bank | Add a capacitor bank to the North Norco substation. | 2017-12-01 | 2017-12-01 | 1826000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Little Gypsy to Claytonia 115 kV line causes a voltage violation at the Norco, Claytonia, and Ormond 115 kV stations. This project will alleviate the voltage violations by installing two 32.4 MVar cap banks at the North Norco 115 kV station. | 2016-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELL-004 | Entergy | Bottom-Up | Submitted for Recommendation
9805 | 2015-09-13 | A in MTEP16 |  | South | Entergy-LA | Patterson to Pontchartrain Park 115 kV: Reconductor Line | Reconductor the Patterson to Pontchartrain Park 115 kV line | 2018-12-01 | 2018-12-01 | 11851000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Avenue C to Paris tap 115 kV line causes a thermal violation on the Pontchartrain Park to Patterson115 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2017-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ENO-001 | Entergy | Bottom-Up | Submitted for Recommendation
9847 | 2015-09-14 | A in MTEP16 |  | South | Entergy-LA | EGSL Underrated Breaker Project: Mossville 69 kV Breaker 17985 | Breaker number 17985 at the Mossville 69 kV substation will be replace due to the short circuit analysis. | 2017-12-01 | 2017-12-01 | 700000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Based on short circuit analysis, transmission breakers were identified as being needed to increase their short circuit interrupting capability. The project involves replacing various EGSL breakers. | 2017-12-01 |  | LA | LA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-030-1 | Entergy | Bottom-Up | Submitted for Recommendation
9848 | 2015-09-14 | A in MTEP16 |  | South | Entergy-LA | EGSL Underrated Breaker Project: Mossville 69 kV Breaker 17995 | Breaker 17995 at the Mossville 69 kV substation will be replaced due to the short circuit analysis. | 2017-12-01 | 2017-12-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Based on short circuit analysis, transmission breakers were identified as being needed to increase their short circuit interrupting capability. The project involves replacing various EGSL breakers. | 2017-12-01 |  | LA | LA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-030-2 | Entergy | Bottom-Up | Submitted for Recommendation
9849 | 2015-09-14 | A in MTEP16 |  | South | Entergy-LA | EGSL Underrated Breaker Project: Carlyss 69 kV Breaker 7840 | Breaker number 7840 at the Carlyss 69 kV substation will be replace due to the short circuit analysis. | 2017-12-01 | 2017-12-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Based on short circuit analysis, transmission breakers were identified as being needed to increase their short circuit interrupting capability. The project involves replacing various EGSL breakers. | 2017-12-01 |  | LA | LA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-030-3 | Entergy | Bottom-Up | Submitted for Recommendation
10008 | 2016-06-22 | A in MTEP16 |  | South | Entergy-LA | Nelson to Menena 230 kV: Construct New Line | Construct new 230 kV line from Nelson to Menena. | 2020-06-01 | 2020-06-01 | 15500000 | Thermal overloads on PPG to Verdine 230 kV and Nelson to Michigan 230 kV FTLO Patton 500/230 kV autotransformer as identified in MISO generation deliverability study. | 2020-06-01 |  | LA | LA | Planned | BaseRel |  |  | 230 | 0 | 5.5 | 0 | 1 |  | 15-EGL-023 | Entergy | Bottom-Up | Submitted for Recommendation
10223 | 2015-11-17 | A in MTEP16 |  | South | Entergy-LA | LAGEN Holly Ridge new substation | Construct a new 115/13.8 kV distribution serving substation on the Oak Ridge - Dunn 115 kV transmission line in North Central Louisiana. | 2016-12-31 | 2016-12-31 | 254833 | Substation requested by customer to support area load. | 2016-12-31 |  | LA | LA | Planned | Other |  | Distribution | 115 | 0 | 0 | 0 | 1 |  | 16-ELN-011 | Entergy | Bottom-Up | Submitted for Recommendation
10583 | 2016-01-12 | A in MTEP16 |  | South | Entergy-LA | Coly 230 kV: Add Breaker | Add a breaker at the Coly 230 kV substation. | 2018-06-01 | 2018-06-01 | 1692865 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The P2-3 breaker failure contingency on Coly 230 kV breakers 13495 or 21295 will overload the Coly 230/69 kV AT 2 or AT 4. | 2016-06-01 |  | LA | LA | Conceptual | Other |  | Reliability | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-037 | Entergy | Bottom-Up | Submitted for Recommendation
10584 | 2016-01-12 | A in MTEP16 |  | South | Entergy-LA | Tiger 230 kV: Add Breaker | Add a 230 kV breaker at the Tiger substation. | 2018-06-01 | 2018-06-01 | 1692865 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The P2-4 bus tie breaker failure contingency on Tiger 230 kV breaker 14325 will overload Harelson to Drusilla to Jefferson 69 kV line. | 2016-06-01 |  | LA | LA | Conceptual | Other |  | Reliability | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-038 | Entergy | Bottom-Up | Submitted for Recommendation
10585 | 2016-01-12 | A in MTEP16 |  | South | Entergy-LA | Harelson 230 kV: Add Breaker | Add a breaker at the Harelson 230 kV substation. | 2018-06-01 | 2018-06-01 | 1692865 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The P2-4 bus tie breaker failure contingency on Harelson 230 kV breaker 9470 will overload Tiger to Essen Tap to Westdale to East to Jefferson, Belfair to Sears, La Station to Capitol, Polyform to Denham Springs to Gloria 69 kV lines. | 2016-06-01 |  | LA | LA | Conceptual | Other |  | Reliability | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-039 | Entergy | Bottom-Up | Submitted for Recommendation
10588 | 2016-03-01 | A in MTEP16 |  | South | Entergy-LA | Fleur 230 kV Substation: New Substation | Construct a new 230 kV substation on the Oakville to Alliance 230 kV transmission line. This substation will be the primary feed to a customer in the area. Load will move from other substations in the area. Rebuild the Ninemile to Barataria 115 kV line. | 2018-12-31 | 2018-12-31 | 42705000 | Entergy Asset Management Asset Management has identified that a new substation will be required to serve an area load. The customer has experienced numerous issues with reliability due to being served off of the 34.5 kV system. Asset Management has identified the need to rebuild the line section to increase reliability. Customers in the area have experienced numerous issues with reliability due to the quality of the line. | 2018-12-31 |  | LA | LA | Conceptual | Other |  | Distribution | 230 | 0 | 0 | 0 | 3 |  | 16-ELL-010 | Entergy | Bottom-Up | Submitted for Recommendation
10591 | 2016-01-12 | A in MTEP16 |  | South | Entergy-LA | Willow Glen 500/138 kV Auto: Adjust Taps | Changing the position of the de-energized tap changer to 500kV (3/C) from 487.5kV (2/B). | 2016-06-01 | 2016-06-01 | 15027 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Attachment Y Retirement Study for Willow Glen 2 and 4 Generating Units, identified an overload of the Willow Glen 500/138kV autotransformer for the loss of the 500/230kV transformer and the outage of the Carville generating unit. | 2016-06-01 |  | LA | LA | Conceptual | Other |  | Reliability | 500 | 138 | 0 | 0 | 1 |  | 16-EGL-041 | Entergy | Bottom-Up | Submitted for Recommendation
10623 | 2016-06-22 | A in MTEP16 |  | South | Entergy-LA | Sadie 230 kV: Construct New Substation | Construct a new 230 kV substation on the PPG to Rosebluff 230 kV line. | 2018-06-01 | 2018-06-01 | 24814742 | Industrial Customer Connection This is a customer driven project to install a new 230 kV substation on the PPG to Rosebluff 230 kV line. | 2018-06-01 |  | LA | LA | Conceptual | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-042 | Entergy | Bottom-Up | Submitted for Recommendation
10624 | 2016-06-22 | A in MTEP16 |  | South | Entergy-LA | Big Lake 230 kV: Construct New Substation | Construct a new 230 kV substation on the Vincent to Graywood 230 kV line. | 2019-06-01 | 2019-06-01 | 28000000 | Industrial Customer Connection This is a customer driven project to install a new 230 kV substation on the Vincent to Graywood 230 kV line. | 2019-06-01 |  | LA | LA | Conceptual | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-043 | Entergy | Bottom-Up | Submitted for Recommendation
11423 | 2016-06-22 | A in MTEP16 |  | South | Entergy-LA | Menena 230 kV: Construct New Substation | Industrial Customer Connection This is a customer driven project to install a new 230 kV substation on the PPG to Rosebluff 230 kV line. | 2017-12-01 | 2017-12-01 | 7290000 | Industrial Customer Connection This is a customer driven project to install a new 230 kV substation on the PPG to Rosebluff 230 kV line. | 2017-12-01 |  | LA | LA | Proposed | Other |  | Reliability | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-044 | Entergy | Bottom-Up | Submitted for Recommendation
9822 | 2015-09-14 | A in MTEP16 |  | South | Entergy-MS | Harper 115 kV new switching station | Construct a new 115 kV breaker switching station. | 2018-12-01 | 2018-12-01 | 5300000 | A breaker station is needed on the Natchez - Liberty 115 kV to improve area reliability. | 2018-12-01 |  | MS | MS | Proposed | Other |  | Reliability | 115 | 0 | 0 | 0 | 1 |  | 16-EMI-001 | Entergy | Bottom-Up | Submitted for Recommendation
9833 | 2015-09-14 | A in MTEP16 |  | South | Entergy-MS | Greenville North Install 2nd Capacitor | Install 2nd 20.5 MVAR capacitor bank at Greenville North 115 kV. | 2018-06-01 | 2018-06-01 | 1185857 | The loss of the Greenville 115 kV bus results in low voltages at Greenville, Greenville Midtown, Greenville East, and Stringtown 115 kV substations. | 2016-06-01 |  | MS | MS | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EMI-007 | Entergy | Bottom-Up | Submitted for Recommendation
9839 | 2015-09-14 | A in MTEP16 |  | South | Entergy-MS | Reconfigure Gerald Andrus 230 kV line terminals | Reterminate Ray Braswell 230 kV line circuit into Bagby line bay. This project will be completed as part of the pre-planned Madison/Hinds Improvement Project as the scope of that project is replacing the necessary breakers at the Gerald Andrus 230 kV. | 2018-03-01 | 2018-03-01 | 0 | The loss of a common shared breaker (P2.3) on the Gerald Andrus - Ray Braswell (future Tinnin bkr station) and Gerald Andrus - Indianola 230 kV lines results in thermal overloading on the Gerald Andrus 230/115 kV autotransformer and multiple line sections on the Greenville - Indianola 115 kV line circuit. | 2016-06-01 |  | MS | MS | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-EMI-005 | Entergy | Bottom-Up | Submitted for Recommendation
9955 | 2015-09-15 | A in MTEP16 |  | South | Entergy-MS | Steiner 115kV Delivery Point | The Steiner DP will be located approximately 1.6 miles northeast of the existing Shaw Switching Station and will be served from Entergy's existing 115kV Cleveland to Shaw transmission line via a looped transmission feed. This DP will require installation of a new switching station with motor operated switches and other miscellaneous upgrades to accommodate the new 115kV looped service. |  |  | 810000 | A SMEPA member cooperative has requested a new delivery in Sunflower County to serve additional load growth. | 2017-12-01 |  | MS | MS | Planned | Other |  | Distribution | 115 | 0 | 0 | 0 | 1 |  |  | South Mississippi Electric Power Association | Bottom-Up | Submitted for Recommendation
10863 | 2016-03-08 | A in MTEP16 |  | South | Entergy-MS | Attala - Conehoma Creek: Upgrade line | Upgrade line rating of Attala - Conehoma Creek 115 kV line to minimum 1303A. | 2017-06-01 | 2017-06-01 | 2.45 | NERC TPL-001-4 P3.2 Loss of Plant Ratcliffe generator (CCGT outage) + loss of Rankin - Pelahatchie 115 kV line circuit. | 2017-06-01 | Submitted alternative of installing 2nd Rankin 230/115 kV autotransformer and rebuilding South Grenada - Elliott led to a decrease in reliability to customer along the Attala - Winona and Attala - Pelahatchie 115 kV lines. | MS | MS | Planned | BaseRel |  |  | 115 | 0 | 0 | 2 | 1 |  | 16-EMI-013 | Entergy | Bottom-Up | Submitted for Recommendation
10864 | 2016-03-08 | A in MTEP16 |  | South | Entergy-MS | Pelahatchie - Morton: Upgrade line | Upgrade the Pelahatchie - Morton 115 kV line to 1303 A. | 2017-12-31 | 2017-12-31 | 6000000 | NERC TPL-001-4 P3.2 Loss of Plant Ratliffe (CCGT) + Choctaw to Clay 500 kV. | 2017-12-31 |  | MS | MS | Planned | BaseRel |  |  | 115 | 0 | 0 | 6.07 | 1 |  | 16-EMI-014 | Entergy | Bottom-Up | Submitted for Recommendation
10865 | 2016-03-08 | A in MTEP16 |  | South | Entergy-MS | Morton - Forest Ind (Southern Company Tie): Upgrade line | Upgrade approximately 9 miles of 115 kV line between Morton and Forest Ind (to the Southern Company tie point) to minimum 1303 A. | 2018-06-01 | 2018-06-01 | 8900000 | NERC TPL-001-4 P3.2 Loss of Plant Ratcliffe (CCGT) + loss of Choctaw to Clay 500 kV line. | 2018-06-01 | Pelahatchie Reactor project no longer sufficiently addresses thermal overloading. Sizing a large reactor will put added transmission flows on other highly loaded lines as well as reduce voltage profile into Southern Company system. | MS | MS | Planned | BaseRel |  |  | 115 | 0 | 0 | 9 | 1 |  | 16-EMI-015 | Entergy | Bottom-Up | Submitted for Recommendation
10943 | 2016-03-23 | A in MTEP16 |  | South | Entergy-MS | Norrel Road: Construct new 230 kV substation | Construct new 230 kV substation on the Clinton Industrial - Gerald Andrus (new Tinnin substation will be cut-in during 2017-2018) 230 kV line. | 2019-10-01 | 2019-10-01 | 8100000 | Entergy Mississippi, Inc has requested a new load serving point to serve a recently signed industrial customer. | 2019-10-01 |  | MS | MS | Planned | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 |  | 16-EMI-016 | Entergy Mississippi | Bottom-Up | Submitted for Recommendation
4620 | 2016-05-10 | A in MTEP16 | B>A | South | Entergy-TX | Kolbs 230 kV - Add capacitor bank | Kolbs Substation: Add two 86.4 MVAR 230 kV capacitor banks | 2017-06-01 | 2017-06-01 | 3000000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The N1G1 contingency loss (P3-2) of the existing 230 kV line form Mid County to Port Arthur coupled with the loss of the Sabine 4 generator will result in low voltage (<0.92 pu) at the Kolbs and Port Arthur 230 kV substations. This project will mitigate the low voltage violation and increase the voltage at the substations to be above 0.92 pu for the P3 contingency. | 2018-06-01 | None | TX | TX | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 | Y | 12-ETI-006 | Entergy | Bottom-Up | Submitted for Recommendation
7930 | 2016-06-22 | A in MTEP16 | B>A | South | Entergy-TX | Heights 230 kV: Construct New Substation | Construct new 230 kV substation for load growth in the Woodlands area to offload the New Caney 138 kV substation. New substation will be tapped into 230 kV line between China and Porter. | 2019-06-01 | 2019-06-01 | 14208000 | Distribution System Load Growth This distribution project is needed to relieve distribution facility loadings in the New Caney Network east of the The Woodlands, TX and provide service to a rapidly developing commercial and residential area. | 2019-06-01 |  | TX | TX | Proposed | Other |  | Distribution | 230 | 34.5 | 0 | 0 | 1 |  | 15-ETI-008 | Entergy | Bottom-Up | Submitted for Recommendation
9806 | 2016-05-27 | A in MTEP16 |  | South | Entergy-TX | Bryan 138/69 kV: Replace Autos & Reconfigure 69 kV Bus | Replace the 2 138/69 kV autotransformers at the Bryan substation and reconfigure the 69 kV and 138 kV buses. | 2019-06-01 | 2019-06-01 | 8268000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Bryan 138/69kV Autos will overload for the loss of the other. For the same contingencies, low voltage occurs at Calvert and thermal overloads occur on the 69kV lines from Bryan A 69kV to Hearne 69kV. These violations are mitigated by replacing both Bryan Autos with 100MVA units and reconfiguring the Bryan 69kV and 138 kV bus. | 2017-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 138 | 69 | 0 | 0 | 2 |  | 16-ETI-001 | Entergy | Bottom-Up | Submitted for Recommendation
9807 | 2015-09-13 | A in MTEP16 |  | South | Entergy-TX | Pintail 138 kV: Construct new Switching Substation | Expand an existing substation to include breakers and switchs. This will allow a normally open point to be closed. | 2018-12-01 | 2018-12-01 | 9524000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Low voltage at Magnolia Ames, Hankamer Marsh, Shiloh, White's Bayou, Brooks Creek and Bayshore 138 kV during the single contingency (P2-1) open breaker at Raywood (B5200). This project will mitigate the low voltage issues. | 2016-06-01 |  | TX | TX | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | 16-ETI-002 | Entergy | Bottom-Up | Submitted for Recommendation
9808 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | Kirbyville 69 kV: Add Cap Bank | Add a new capacitor bank to the Kirbyville 69 kV substation. | 2018-06-01 | 2018-06-01 | 1000000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of Fawil 138-69kV Auto (P1-3) causes low voltage at Kirbyville and Fawil. The violation is mitigated by installing a 7.2 MVAR 69 kV Capacitor Bank at Kirbyville Substation. | 2018-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-ETI-005 | Entergy | Bottom-Up | Submitted for Recommendation
9809 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | Hull to Sour Lake 69 kV: Reconductor Line | Reconductor the Hull to Sout Lake 69 kV line. | 2019-06-01 | 2019-06-01 | 30759000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Low voltage at Raywood, Daisetta, Daisy, Hull, Hardin, Quality Mills, Batson, Saratoga, Transco and Dome 69 kV and thermal overloads on Sour Lake to Hull 69 kV line section during the following contingencies: (P1-3) loss of the Raywood 138/69 kV auto, (P1-2) loss of the Raywood to Daisetta 69 kV line, (P1-3) loss of the China 230/138 kV auto, (P1-2) loss of the Devers to China 138 kV line, (P1-2) loss of the Raywood to Devers 138 kV line and (P1-2) loss of the Cheek to South Beaumont 138 kV line. The violations will be mitigated by reconductoring the Hull to Sour Lake 69 kV line sections. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-ETI-007 | Entergy | Bottom-Up | Submitted for Recommendation
9810 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | Raywood to Daisetta 69 kV: Reconductor Line | Reconductor the Raywood to Daisetta 69 kV line. | 2019-12-01 | 2019-12-01 | 8655000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Thermal overloads on Raywood to Daisetta 69 kV line section during the contingency (P1-2) loss of the Sour Lake to Amelia 69 kV line. The violation will be mitigated by reconductoring the Raywood to Daisetta 69 kV line section. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-ETI-008 | Entergy | Bottom-Up | Submitted for Recommendation
9812 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | PARIP Garden 230 kV: Construct New 230 kV Substation | Port Arthur Reliability Improvement Plan: Cut the Sabine to China 230 kV line and the Nederland to Mid County 230 kV line into a new 230 kV substation named Garden. | 2019-06-01 | 2019-06-01 | 65835000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple N-2 scenarios on the 230 kV network between Sabine and Port Acres Bulk 230 kV can cause cascading events that result in non-consequential load loss in excess of 850 MW (P6). Included in the total of 850 MW of non-consequential load loss are approximately 450 MW of industrial loads in the Port Arthur area. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ETI-014-1 | Entergy | Bottom-Up | Submitted for Recommendation
9813 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | PARIP Garden to Legend 230 kV: Construct New Line | Port Arthur Reliability Improvement Plan: Construct a new line from the new Garden substation to the new Legend substation. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple N-2 scenarios on the 230 kV network between Sabine and Port Acres Bulk 230 kV can cause cascading events that result in non-consequential load loss in excess of 850 MW (P6). Included in the total of 850 MW of non-consequential load loss are approximately 450 MW of industrial loads in the Port Arthur area. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ETI-014-2 | Entergy | Bottom-Up | Submitted for Recommendation
9814 | 2016-05-10 | A in MTEP16 |  | South | Entergy-TX | PARIP Legend 230 kV: Construct New Substation | Port Arthur Reliability Improvement Plan: Construct a new substation and cut in 230 kV line 829(Port Acres to Keith Lake). The new substation will be named Legend. | 2019-06-01 | 2019-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Multiple N-2 scenarios on the 230 kV network between Sabine and Port Acres Bulk 230 kV can cause cascading events that result in non-consequential load loss in excess of 850 MW (P6). Included in the total of 850 MW of non-consequential load loss are approximately 450 MW of industrial loads in the Port Arthur area. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ETI-014-3 | Entergy | Bottom-Up | Submitted for Recommendation
9817 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | Helbig 230 kV: Reconfigure Bus | Reconfigure the bus work at the Helbig 230 kV substation to represent a ring bus. | 2018-12-01 | 2018-12-01 | 7196000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Helbig AT1 will exceed its thermal rating during the loss of the Helbig AT2 and Helbig 230 kV bus #2. The South Beaumont - Yankee Doodle - Crockett 69 kV line section will exceed its thermal rating during the loss of the Helbig AT1 and Helbig 230 kV bus #1. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ETI-016 | Entergy | Bottom-Up | Submitted for Recommendation
9818 | 2015-12-16 | A in MTEP16 |  | South | Entergy-TX | Stowell to Himex 69 kV: Convert to 138 kV | Convert the Stowell to Himex 69 kV line to 138 kV. The line is already built to 138 kV standards. | 2019-06-01 | 2019-06-01 | 13600000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Stowell 138 kV bus (P2-2) will cause thermal overloads and low voltage on 69 kV line 62 and 63 from South Beaumont to Winshire. Loss of the Stowell 138/69 kV, 50 MVA Autotransformer #3 (P1-3) will cause overloads on Stowell 138/69 kV, 35 MVA autotransformer #3. Converting the Stowell to Himex 69 kV line to 138 kV will mitigate the overloads and low voltage issues. | 2019-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-ETI-017 | Entergy | Bottom-Up | Submitted for Recommendation
9852 | 2015-09-14 | A in MTEP16 |  | South | Entergy-TX | Grimes 345/138 kV: Install Breakers on Low Side of AT2 | Install breakers on the low side of autotransformer number 2 at the Grimes 345/138 kV substation. | 2017-06-01 | 2017-06-01 | 1142000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Ponderosa to Fish Creek 138 kV, Fish Creek to Spring Branch 138 kV, Grimes 345/230 kV AT and Ponderosa 230/138 kV AT overload in 2016 Summer for a breaker failure at Grimes 138 kV B16810 (P2-3). Installing breakers on the low side of Grimes AT2 so that it is protected by the breaker-and-a-half scheme will mitigate the thermal overloads. | 2016-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  | 16-ETI-018 | Entergy | Bottom-Up | Submitted for Recommendation
10823 | 2016-03-01 | A in MTEP16 |  | South | Entergy-TX | Moscow 138 kV: Construct New Substation | Construct a new 138 kV substation on L-411 Corrigan Bulk to Kickapoo 138 kV line to serve an industrial customer. | 2017-06-01 | 2017-06-01 | 7004002 | Industrial Customer Connection This is a customer driven project to construct a new 138 kV substation to serve new industrial load in the Corrigan, TX area. | 2017-06-01 |  | TX | TX | Conceptual | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | 16-ETI-021 | Entergy | Bottom-Up | Submitted for Recommendation
11363 | 2016-06-08 | A in MTEP16 |  | South | Entergy-TX | Hartburg 500 kV: Reconfigure Line Bays | Re-position the line bays of line L-800 (Hartburg-Cottonwood 500 kV Circuit 1) and line L-547 (Hartburg-Cypress 500 kV line) at Hartburg 500 kV substation. | 2017-06-01 | 2017-06-01 | 2000000 | Project identified in Attachment Y study, the Hartburg 500-230 kV auto Circuit 2 thermally overloads during the failure of breaker #13125 which causes the loss of the Hartburg 500-230 kV auto Circuit 1 and the Hartburg-Cypress 500 kV line. | 2017-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 500 | 0 | 0 | 0 | 1 |  | 16-ETI-023 | Entergy | Bottom-Up | Submitted for Recommendation
9957 | 2016-04-27 | A in MTEP16 |  | South | SMEPA | Origis Solar Project Substation | The Origis Energy solar plant will tap SMEPA's existing 69kV Line 42 (Sumrall to Rawls Springs) approximately 5.6 miles from Sumrall with a new 69kV switching station and a 69/26.4 kV GSU. Line 42 and 43 (Columbia to Sumrall) will be uprated to a higher conductor temperature via structural change outs to support the generation addition. OPGW will also be installed for communications. | 2017-03-23 | 2017-03-23 | 1590000 | This project is necessary to support a new 52MW Origis Energy solar power plant that will tap SMEPA's 69kV Line 42 (Sumrall to Rawls Springs). | 2017-03-23 |  | MS | MS | Proposed | GIP | Not Shared |  | 69 | 26.4 | 0 | 0 | 2 |  |  | South Mississippi Electric Power Association | Externally Driven | Recommended
9969 | 2016-05-08 | A in MTEP16 |  | South | SMEPA | Origis Solar Project Transmission Rebuilds | The Origis Energy solar plant will tap SMEPA's existing 69kV Line 42 (Sumrall to Rawls Springs) approximately 5.6 miles from Sumrall with a new 69kV switching station and a 69/26.4 kV GSU. Line 42 and 43 (Columbia to Sumrall) will be uprated to a higher conductor temperature via structural change outs to support the generation addition. OPGW will also be installed for communications. |  |  | 4782000 | This project is necessary to support a new 52MW Origis Energy solar power plant that will tap SMEPA's 69kV Line 42 (Sumrall to Rawls Springs). | 2017-03-22 |  | MS | MS | Proposed | GIP | Not Shared |  | 69 | 0 | 0 | 0 | 2 |  |  | South Mississippi Electric Power Association | Externally Driven | Recommended
9949 | 2015-09-15 | A in MTEP16 |  | South | SMEPA | Cloverdale 115kV Delivery Point | The Cloverdale DP will be served from the existing Entergy IP to Johns Manville 115kV transmission line via a looped transmission feed into a new switching station to be constructed at the DP site. |  |  |  | A SMEPA member cooperative has requested a new delivery point to serve a new industrial customer in Adams County, MS. | 2017-12-01 |  | MS | MS | Planned | Other |  | Distribution |  |  |  |  | #N/A |  |  | South Mississippi Electric Power Association | Bottom-Up | Submitted for Recommendation
3190 | 2016-02-02 | A in MTEP16 | B>A | West | ATC | Rebuild Sunset Point-Winneconne 69 kV | Rebuild line Y-103 from Sunset Point to Winneconne to SN/SE = 200/300 deg F | 2016-04-29 | 2016-04-29 | 3868404 | Thermal overloading occurs under Category B conditions. | 2016-12-31 |  | WI | WI | Conceptual | Other | Not Shared | Reliability | 69 | 0 | 0 | 10.5 | 1 | Y | PR05190 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
7583 | 2015-09-15 | A in MTEP16 | B>A | West | ATC | Rebuild Lone Rock - Boscobel 69 kV | Rebuild Y-124 from Lone Rock to Boscobel with T2-4/0 ACSR. Inlcudes partial rebuild of Y-78 Lone Rock - Richland Center | 2015-12-31 | 2018-12-31 | 41848961 | Reliability | 2018-12-31 |  | WI | WI | Conceptual | Other |  | Reliability | 69 | 0 | 0 | 39.73 | 7 |  | PR04985 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
7983 | 2015-09-15 | A in MTEP16 | B>A | West | ATC | Install 138/69 kV Canal Breakers | Install Canal 138-69 kV transformer high/low side breaker additions | 2017-06-01 | 2017-06-01 | 5100000 | Operating flexibility, reliability (69 kV B3 with prior maintenance) | 2017-12-31 |  | WI | WI | Proposed | Other |  | Distribution | 138 | 69 | 0 | 0 | 1 |  | PR05247 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
7985 | 2015-09-18 | A in MTEP16 | B>A | West | ATC | Install 138 kV Canal Redundant Bus Differentials | This project consists of installing redundant bus differential protection on the two Canal 138-kV buses. The project will install two new dual SEL-487B bus differential relay panels. | 2017-06-01 | 2017-06-01 | 221116 | Reliability (C9) | 2017-12-31 |  | WI | WI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR04578 F3720 WO:69613 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
7986 | 2016-02-12 | A in MTEP16 | B>A | West | ATC | Install 138/69 kV Highway V Breakers | Install 138-69 kV transformer high/low side breaker additions to T1 and T2. | 2018-12-31 | 2018-12-31 | 0 | Operating flexibility, reliability (69 kV B3 with prior maintenance) | 2017-12-31 |  | WI | WI | Conceptual | Other |  | Distribution | 138 | 69 | 0 | 0 | 1 |  | PR05253 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
8442 | 2015-10-13 | A in MTEP16 | B>A | West | ATC | Replace Arnott 138/69 kV Transformer | Asset maintenance, Replace the Arnott 138-69 kV Tr with 60 MVA unit | 2016-12-31 | 2016-12-31 | 4545000 | Reliability | 2016-12-31 |  | WI | WI | Proposed | Other |  | Reliability | 138 | 69 | 0 | 0 | 1 |  | PR05503 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
8640 | 2015-09-15 | A in MTEP16 | B>A | West | ATC | Upgrade City Limits Bus 138 kV | Replace bus conductors at City Limits | 2017-12-31 | 2017-12-31 | 500000 | Reliability | 2017-12-31 |  | WI | WI | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 2 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
8841 | 2015-03-16 | A in MTEP16 |  | West | ATC | Rebuild Finger Rd - Canal 69 KV | This project is a Asset Management driven project to rebuild the main section of J-10 from Finger Road to Beardsley to Canal. The tapped lines off of J-10 and East Krok to Beardsley are not included in this scope. No substation work is included in scope. | 2019-12-01 | 2019-12-01 | 74000000 | Reliability - Asset maintenance. | 2019-12-31 |  | WI | WI | Proposed | Other |  | Reliability | 69 | 0 | 0 | 55.03 | 7 |  | PR04988 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9423 | 2015-07-28 | A in MTEP16 |  | West | ATC | Rebuild 115KV Line B-106 Plover - Whiting Avenue Substation | Rebuild line B-106 (Plover-Okray-Whiting 115) using existing conductor 795 ACSR. | 2019-12-01 | 2019-12-01 | 6217603 | Reliability | 2019-12-31 |  | WI | WI | Planned | BaseRel |  |  | 115 | 0 | 0 | 5.8 | 1 |  | PR04968, F3633 & F363 WO: 069403-55, | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9896 | 2015-09-15 | A in MTEP16 |  | West | ATC | Lyndon Substation | Install 2 line breakers to sectionalize. | 2015-12-31 | 2015-12-31 | 3100000 | Reliability |  |  | WI | WI | M5_In Service | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9911 | 2015-09-15 | A in MTEP16 |  | West | ATC | Maes Substation 138 kV | Maes substation: Install 2 line breakers to sectionalize. | 2016-04-22 | 2016-04-22 | 1800000 | Reliability |  |  | WI | WI | Planned | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR#5981 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9917 | 2016-06-10 | A in MTEP16 |  | West | ATC | Bloomington Substation 69kV | Install SCADA controlled breakers to sectionalize. | 2016-12-31 | 2016-12-31 | 1600000 | Reliability |  |  | WI | WI | Planned | Other |  | Distribution | 69 | 0 | 0 | 0 | 1 |  | PR04727, PR04726, F3576, WO064898 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9918 | 2015-09-15 | A in MTEP16 |  | West | ATC | Red Maple Substation 138kV | Install a bus tie breaker. | 2016-06-01 | 2016-06-01 | 1200000 | Reliability. |  |  | WI | WI | Planned | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR#6143 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9921 | 2015-09-15 | A in MTEP16 |  | West | ATC | Birchwood Substation 138kV | Install a bus tie breaker. | 2017-12-31 | 2017-12-31 | 700000 | Reliability. |  |  | WI | WI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR#6142 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9923 | 2015-09-15 | A in MTEP16 |  | West | ATC | Mukwanago Substation 138kV | Install line breaker on line 67K61. | 2017-12-01 | 2017-12-01 | 600000 | Reliability. |  |  | WI | WI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9925 | 2015-10-05 | A in MTEP16 |  | West | ATC | Tap Stone Lake - Gardner Park 345-kV line | Loop Stone Lake - Gardner Park 345-kV line into new Pershing 345-kV Substation. | 2018-06-01 | 2018-06-01 | 15000000 | T-T Interconnection. |  |  | WI | WI | Proposed | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9934 | 2015-09-15 | A in MTEP16 |  | West | ATC | Upgrade Oak Creek - Hayes 138-kV line | Oak Creek - Hayes 138-kV line 811 upgrade and reconfiguration | 2018-06-30 | 2018-06-30 | 21000000 | Reliability. |  |  | WI | WI | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | PR07285 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9938 | 2015-09-15 | A in MTEP16 |  | West | ATC | Replace Sunset Point 138-69 kV Transformer | Replace 138/69KV power transformer with 100MVA continuous top rated transformer. | 2016-12-01 | 2016-12-01 | 6000000 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  | PR04754 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9944 | 2015-09-15 | A in MTEP16 |  | West | ATC | Replace Erdman T31 Transformer | Replace Erdman T31 Transformer. | 2017-12-31 | 2017-12-31 | 6000000 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9954 | 2015-12-03 | A in MTEP16 |  | West | ATC | Replace Lost Dauphin T1 Transformer | Replace Lost Dauphin T1 Transformer. | 2018-12-01 | 2018-12-01 | 6700000 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  | PR07375 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9958 | 2015-09-15 | A in MTEP16 |  | West | ATC | Replace East Krok Transformer | Replace East Krok Transformer. | 2017-12-31 | 2017-12-31 | 0 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9961 | 2015-09-15 | A in MTEP16 |  | West | ATC | Replace Nelson Dewey T31/T32 Transformers | Replace Nelson Dewey T31/T32 Transformers. | 2018-12-31 | 2018-12-31 | 6000000 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9977 | 2015-09-15 | A in MTEP16 |  | West | ATC | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation. | 2019-12-31 | 2019-12-31 | 35000000 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
9986 | 2016-02-12 | A in MTEP16 |  | West | ATC | Rebuild 138KV Line 762 Port Washington - Saukville Substation | Rebuild 138KV Line 762 Port Washington - Saukville Substation. | 2021-12-31 | 2021-12-31 | 15000000 | Reliability. |  |  | WI | WI | Planned | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  | PR07410 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10403 | 2016-05-04 | A in MTEP16 |  | West | ATC | Re-rate Kegonsa - Sun Prairie (Y-81) 69kV Line | Re-rate Y -81 69kV line between Kegonsa - Sun Prairie. | 2017-04-21 | 2017-04-21 | 5000000 | Reliability. Operations. |  |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | PR07285,F4849, WO 602023 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10404 | 2016-05-04 | A in MTEP16 |  | West | ATC | Re-rate 9 Mile - Detour (6950) 69kV Line | Re-rate Approximately 56.87 miles (6950) 69kV Line between 9 Mile - Detour substations. | 2017-03-17 | 2017-03-17 | 7000000 | Reliability. Asset renewal. |  |  | MI | MI | Planned | Other |  | Reliability | 69 | 0 | 0 | 56.87 | 1 |  | PR07333,F4812, WO601919 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10484 | 2015-12-16 | A in MTEP16 |  | West | ATC | Construct Eaton 138 kV T- D | Construct a new ATC 138KV loop through at Eaton Substation. | 2019-06-01 | 2019-06-01 | 0 | T-D, system reliability |  |  | WI | WI | Proposed | Other |  | Distribution | 138 | 24.9 | 0 | 21.46 | 3 |  | PR07373 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10485 | 2015-12-16 | A in MTEP16 |  | West | ATC | Construct Bay Ridge 138 kV T- D | Construct a new ATC 138KV loop through at Bay Ridge Substation. | 2022-06-01 | 2022-06-01 | 0 | T-D, system reliability |  |  | WI | WI | Proposed | Other |  | Distribution | 138 | 24.9 | 0 | 2.67 | 3 |  | PR007372 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10543 | 2016-01-05 | A in MTEP16 |  | West | ATC | Construct T-D Escanaba North Substation | Construct T-D Escanaba North Substation (GOAB) | 2017-01-01 | 2017-01-01 | 0 | Reliability. T-D. |  |  | MI | MI | Planned | Other |  | Distribution | 69 | 0 | 1.29 | 0 | 2 |  | PR07390 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10563 | 2016-01-12 | A in MTEP16 |  | West | ATC | Construct T -D Oakview Substation | Construct T -D Oakview Substation | 2018-06-01 | 2018-06-01 | 0 | Reliability. T-D. |  |  | WI | WI | Planned | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR07397 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10589 | 2016-01-12 | A in MTEP16 |  | West | ATC | Rerate Whitcomb - Tigerton Tap 69kV | Rerate Whitcomb - Tigerton Tap 69kV | 2017-06-09 | 2017-06-09 | 0 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | PR07388 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10603 | 2016-01-13 | A in MTEP16 |  | West | ATC | Construct T - D Springwater Substation | Construct T - D Springwater Substation. | 2019-12-31 | 2019-12-31 | 0 | Reliability. T-D. |  |  | WI | WI | Proposed | Other |  | Distribution | 69 | 0 | 1.25 | 0 | 1 |  | PR07299 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10643 | 2016-02-12 | A in MTEP16 |  | West | ATC | Construct T - D St. Martins Substation | St Martins Bus Expansion, Bus-tie Breaker Addition, Line Relocation, and T-D Transformer Addition. | 2017-01-01 | 2018-01-01 | 0 | Reliability. T-D. | 2018-01-01 |  | WI | WI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 3 |  | PR07400 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10683 | 2016-02-02 | A in MTEP16 |  | West | ATC | Uprate Lone Rock - Richland Center 69kV Line | Uprate Lone Rock - Richland Center to max operating temperature. | 2017-06-09 | 2017-06-09 | 0 | Reliability. |  |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | PR07394 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10684 | 2016-02-02 | A in MTEP16 |  | West | ATC | Construct T - D Ellinwood Substation | T-D distribution transformer addition at Ellinwood Substation. | 2017-06-01 | 2017-06-01 | 0 | Reliability. T-D. |  |  | WI | WI | Proposed | Other |  | Distribution | 138 | 24.9 | 0 | 0 | 1 |  | PR07396 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10685 | 2016-02-02 | A in MTEP16 |  | West | ATC | Construct T - D Tomahawk Substation | Tomahawk Substation bus-tie breaker addition and T-D distribution transformer addition. | 2017-06-01 | 2017-06-01 | 0 | Reliability. Distribution. |  |  | WI | WI | Proposed | Other |  | Distribution | 115 | 0 | 0 | 0 | 1 |  | PR07393 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10686 | 2016-02-02 | A in MTEP16 |  | West | ATC | Construct T - D Roosevelt Road Substation | ATC bus expansion and T-D distribution transformer addition. | 2018-06-01 | 2018-06-01 | 0 | Reliability. T-D. | 2018-06-01 |  | WI | WI | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 1 |  | PR07392 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10703 | 2016-02-08 | A in MTEP16 |  | West | ATC | Replace Jefferson SS 138 kV Circuit Breakers | Replace Jefferson SS 138 kV Circuit Breakers and replace 138kV capacitor bank. | 2016-11-15 | 2016-11-15 | 0 | Reliability. |  |  | WI | WI | Planned | Other |  | Distribution | 138 | 0 | 0 | 0 | 2 |  | PR07050 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
11223 | 2016-05-12 | A in MTEP16 |  | West | ATC | Construct T - D Townhall Substation | New T-D Townhall Substation - GOAB on Y-32 and approx. 2 miles of new 69 kV ROW. | 2017-06-01 | 2017-06-01 | 3900000 | Reliability. T-D. |  |  | WI | WI | Proposed | Other |  | Reliability | 69 | 0 | 0 | 2 | 1 |  | PR07437, F4934, WO602202 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
11224 | 2016-05-12 | A in MTEP16 |  | West | ATC | Construct T - D White Lake Substation | White Lake Distribution Transformer Addition and ATC Line Breaker Addition. | 2017-11-01 | 2017-11-01 | 908000 | Reliability. T-D. | 2017-11-01 |  | WI | WI | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  | PR07471 | American Transmission Co. LLC | Bottom-Up | Submitted for Recommendation
10183 | 2015-10-07 | A in MTEP16 |  | West | ATC, XEL | Pershing 345 kV Substation | New 345/115 kV substation located near Sheldon Pump on the Stone Lake to Gardner Park 345 kV line. This is a joint Xcel Energy/ATC project with ATC owning the 345 kV yard at Pershing and Xcel Energy owning the rest of the substation. | 2018-06-01 | 2018-06-01 | 14500000 | Multiple N-2 outages in northern WI cause overloads on the Hydro Lane - Osprey 115 kV line. | 2018-06-01 |  | WI | WI | Planned | BaseRel |  |  | 345 | 115 | 0 | 0 | 2 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
11383 | 2016-06-15 | A in MTEP16 |  | West | CFU-PMEU | J329 Network Upgrades | Network upgrades associated with J329 for substations in Pella Iowa. | 2017-08-01 | 2017-08-01 | 1043700 | Accommodate GI request and upgrade of transmission system at Pella West Substation | 2017-08-01 |  | IA | IA | Proposed | GIP | Not Shared |  | 69 | 0 | 0 | 0 | 3 |  | Pella RRHD | Cedar Falls Utilities | Externally Driven | Recommended
7884 | 2015-03-30 | A in MTEP16 |  | West | GRE | Riverview 345/115/69 kV Substation | Construct the new Riverview 345/115/69 kV substation directly off the CapX 345 kV line between the Melrose East and Millwood 69 kV substations. The transformers will be a 448 MVA, 345/115 kV transformer and a 70 MVA 115/69 MVA transformer. This substation will initially have two 345 line terminating breakers, a single 345 kV breaker on the high side of the transformer, two 69 kV line termination breakers in addition to a low side 69 kV breaker. The substation should be designed for future development and be laid out for nine 345 breaker (3 rows of 345 kV breakers in a breaker and half scheme), six 115 kV (2 rows of 115 kV breakers in a breaker and half scheme), and four 69 kV breakers in a straight bus configuration. | 2018-12-10 | 2018-12-10 | 20051684 | This project is needed to improve load serving in the extensive 69 kV transmission system that is bounded by Douglas County, Paynesville, Wakefield and West St. Cloud 115/69 kV sources. The transmission system in the area experiences equipment overload, transmission line overload and low voltage concerns during contingencies. System intact overloads have also been identified on the West St. Cloud transformer and West St. Cloud to St. Johns 69 kV line during system peak conditions. In addition to the loading and voltage violations, maintenance outages in the area have been problematic as the transmission system is weak to serve existing load for contingencies following a maintenance outage. In a situation where an outage is followed by a maintenance outage, a significant amount load needs to be dropped to bring the system back within load serving voltage and loading criteria. Multiple studies, include the West St. Cloud area study concluded that the existing transmission system is not sufficient to serve existing load at system peak condition. The Riverview 345/115/69 kV substation is designed to address the load serving concerns in the transmission system for a long term. When the substation is in-serivice, the transmission system will have sufficient capacity to serve existing load as well as new loads the may come to the area. | 2017-11-01 |  | MN | MN | Proposed | Other |  | Reliability | 345 | 69 | 0 | 4.6 | 3 | Y | 203079 | Great River Energy | Bottom-Up | Submitted for Recommendation
7896 | 2015-03-30 | A in MTEP16 |  | West | GRE | Fish Trap Pumping Station | Construct a new 115 kV transmission line from the Dog Lake to Scearcyville (#24 Line) 115 kV transmission line to Koch Pipeline's new Fish Trap pumping substation (approximately 20 miles). | 2017-05-22 | 2017-05-22 | 10855000.26 | New pumping station load. | 2018-03-19 |  | MN | MN | Proposed | Other |  | Reliability | 115 | 115 | 20 | 0 | 1 | Y | 202987 | Great River Energy | Bottom-Up | Submitted for Recommendation
9200 | 2015-07-23 | A in MTEP16 |  | West | GRE | Two Inlets Pumping Station (X1A) | Tap the IM-PT line near Potato Lake substation and build ~7.5 miles of 115kV transmission line to connect the future Two Inlets substation. The substation will supply power to the Enbridge Two Inlets pump station. | 2017-10-13 | 2017-10-13 | 7344393.37 | New member load. |  |  | MN | MN | Proposed | Other |  | Reliability | 115 | 0 | 7.5 | 0 | 1 |  | 203613 | Great River Energy | Bottom-Up | Submitted for Recommendation
9201 | 2015-07-23 | A in MTEP16 |  | West | GRE | Backus Pumping Station (X2A) | Build 115 kV line from a new interconnection to the MP?s 115 kV #142 line (Badoura ? Pine River) to the Bull Moose substation - Backus Pump Station | 2018-07-30 | 2018-07-30 | 2105606.54 | New member load. |  |  | MN | MN | Proposed | Other |  | Reliability | 115 | 0 | 3.5 | 0 | 1 |  | 203610 | Great River Energy | Bottom-Up | Submitted for Recommendation
9202 | 2015-07-23 | A in MTEP16 |  | West | GRE | Palisade Pumping Station (X3A) | Build 115 kV line from MP's 115 kV #13 line to the Enbridge Palisade Pumping Station. | 2017-10-31 | 2017-10-31 | 13058755.19 | New member load. |  |  | MN | MN | Proposed | Other |  | Reliability | 115 | 0 | 13 | 0 | 2 |  | 203611 | Great River Energy | Bottom-Up | Submitted for Recommendation
9203 | 2015-07-23 | A in MTEP16 |  | West | GRE | Cromwell Pumping Station (X4A) | Build 115 kV line from line to the Cromwell Pumping Station. | 2017-10-31 | 2017-10-31 | 920000 | New member load. |  |  | MN | MN | Proposed | Other |  | Reliability | 115 | 0 | 0.2 | 0 | 1 |  | 203612 | Great River Energy | Bottom-Up | Submitted for Recommendation
10423 | 2015-12-01 | A in MTEP16 |  | West | GRE | Randolph Distribution Substation | Construct approximately 0.25 mile in and out 115 kV line from the NSP 0822 line (Empire to Colville). | 2017-03-30 | 2017-03-30 | 525000 | Dakota Electric Association is building a new distribution substation to unload nearby DEA Byllesby and Castle Rock substations. | 2017-03-30 |  | MN | MN | Proposed | Other |  | Distribution | 115 | 0 | 0.25 | 0 | 1 |  | 20418 | Great River Energy | Bottom-Up | Submitted for Recommendation
10424 | 2015-12-01 | A in MTEP16 |  | West | GRE | Savage Distribution Substation | Construct approximately 0.5 mile in and out 115 kV line from the NSP 5539 line (Black Dog to Blue Lake). | 2017-10-31 | 2017-10-31 | 1000000 | Minnesota Valley Electric Cooperative is building a new distribution substation. | 2017-10-31 |  | MN | MN | Proposed | Other |  | Distribution | 115 | 0 | 0.5 | 0 | 1 |  | 20559 | Great River Energy | Bottom-Up | Submitted for Recommendation
11463 | 2016-06-29 | A in MTEP16 |  | West | GRE | C023 - Stanton 31RB3 | Jumper replacement inside Stanton Substation at 230 kV breaker 31RB3. | 2016-11-01 | 2016-11-01 | 33033 | Generation interconnection. | 2016-11-01 |  | ND | ND | Planned | GIP | Not Shared |  | 230 | 0 | 0 | 0 | 1 |  | 204473 | Great River Energy | Externally Driven | Recommended
4378 | 2015-03-30 | A in MTEP16 | B>A | West | GRE, MP | Menahga Area Project | Build Hubbard to Blueberry to Red Eye 115 kV | 2017-10-04 | 2020-09-01 | 29360748.68 | 34.5 kV load is exceeding the capability of the 34.5 kV system. Need to establish new sources to multiple load points | 2020-09-01 | Build new 115 kV systems operated at 34.5 kV (MN Pipeline-Menahga) | MN | MN | Proposed | Other |  | Distribution | 115 | 34.5 | 23 | 0 | 5 | Y | 202970 | Great River Energy | Bottom-Up | Submitted for Recommendation
9664 | 2015-09-09 | A in MTEP16 |  | West | ITCM | Guthrie-White Pole Rd-Panora 34 to 69 kV Conversion | Convert 34.5 kV system between Guthrie - White Pole Rd (new breaker station) - Menlo - Redfield - Panora - Guthrie to 69 kV operation | 2017-12-31 | 2017-12-31 | 3385176 | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | 2017-12-31 | Leave as-is, continue to operate radially at 34.5 kV - not a viable alternative due to age and condition issues with the existing system, as well as the inability to serve any potential significant load growth. | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 38.5 | 22 |  | Guthrie-Panora 34 to 69 Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
9665 | 2015-09-09 | A in MTEP16 |  | West | ITCM | PCI-Oak Hill 34 to 69 kV Conv | Convert 34.5 kV system between PCI and Oak Hill to 69 kV operation | 2017-12-31 | 2017-12-31 | 33600 | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | 2018-10-01 | Leave as-is, continue to operate radially at 34.5 kV - not a viable alternative due to age and condition issues with the existing system, as well as the inability to serve any potential significant load growth. | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 4.5 | 3 |  | PCI-Oak Hill 34 to 69 Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
9666 | 2015-09-09 | A in MTEP16 |  | West | ITCM | Emerald Isle-Beverly 34 to 69 kV Conv | Convert 34.5 kV system between Beverly and Emeral Isle to 69 kV operation. | 2018-12-31 | 2018-12-31 | 5114718 | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | 2018-12-31 | Leave as-is, continue to operate radially at 34.5 kV - not a viable alternative due to age and condition issues with the existing system, as well as the inability to serve any potential significant load growth. | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 9.85 | 7 |  | Emerald Isle-Beverly 34 to 69 kV Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
9667 | 2015-09-09 | A in MTEP16 |  | West | ITCM | Wapello County Substation Reliability Rebuild | Rebuild the Wapello County 161kV to breaker and 1/2 design and upgrade the 69 kV ring bus. | 2017-12-31 | 2017-12-31 | 10115465 | The existing Wapello county substation has several issues: the 161 kV ring bus does not have all breakers and certain outages take out adjacent facilities, the existing control enclosure is in poor physical condition and does not have complete drawings, the existing relays do not allow proper testing to meet NERC requirements without taking a complete substation outage, the existing oil circuit breakers are in poor physical condition and in need of replacement | 2017-12-31 | Leave as-is or do minimal piece meal upgrades at the substation to address each issue indavidually - not viable due to relay testing requirements to meet NERC compliance and poor phsyical condition of existing facilities | IA | IA | Planned | BaseRel |  |  | 161 | 69 | 0 | 0 | 6 |  | Wapello Reliability Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9668 | 2015-09-11 | A in MTEP16 |  | West | ITCM | Cedar Rapids-North Liberty area-Hills Upgrades | Add a new Hills area 345/161kV source and upgrade the 161 and 69kV systems in the North Liberty area. This includes a new North Liberty 161/69kV substation also. | 2019-12-31 | 2025-12-31 | 75440438 | The North Liberty IA area which includes the northern Coralville and Tiffin areas, is experiencing continued load growth. The existing system in the area requires updgrades to support both near term issues and long term projected load growth. Some of the upgrades as part of the comprehensive area plan are non-MISO TO upgrades (CIPCO), but are also needed as part of a complete package of system upgrades. | 2022-12-31 | Alternative to project MTEP 8111. | IA | IA | Planned | BaseRel |  |  | 345 | 69 | 0 | 0 | 14 |  | CR-North Liberty-Hills | ITC Midwest | Bottom-Up | Submitted for Recommendation
9669 | 2015-11-18 | A in MTEP16 |  | West | ITCM | St. Ansgar Industrial Substation | New 69kV/distribution substation. Tap 69kV line and install new 69kV breakers for new substation. | 2017-11-11 | 2017-11-17 | 2508817 | Alliant Energy is planning a new industrial customer load addition to the distribution system near St. Ansgar, IA. To support the load addition ITCM will need to construct lines to feed the substation from an existing 69 kV line and install line breakers to protect the customer. | 2017-05-31 | Tap the load off of the existing line without installing bus and breakers - not viable due to the proposed size of the load, and the resulting decreased reliability. | IA | IA | Planned | Other |  | Distribution | 69 | 69 | 0 | 0 | 2 |  | St. Ansgar Industrial | ITC Midwest | Bottom-Up | Submitted for Recommendation
9670 | 2015-09-09 | A in MTEP16 |  | West | ITCM | Columbus Junction 69 kV Breaker Addition | Add 69 kV breaker at the Columbus Junction substation. | 2020-12-31 | 2020-12-31 | 932101 | The existing 69 kV Columbus Junction Substation has a single breaker, a second breaker is need to increase reliability and protect the distribution load. With the current configuration the customer experiences an outage for the loss of the line to Washington until the motor operated switches transfer the load. | 2020-12-31 | Leave as-is - not viable due to the decreased reliability of the existing configuration. | IA | IA | Planned | Other |  | Distribution | 69 | 69 | 0 | 0 | 1 |  | Columbus Junction Breaker add | ITC Midwest | Bottom-Up | Submitted for Recommendation
9671 | 2015-09-09 | A in MTEP16 |  | West | ITCM | Amber Creamery 69 kV Capacitor | Add a 69 kV cap bank at the Amber Creamery substation. | 2016-12-31 | 2016-12-31 | 515076 | Prior to the Anamosa, IA area 34.5-69 kV conversion, which has been delayed (currently estimated in 2018), low voltage issues are seen for the loss of the Wyoming 161/69 kV source. In order to support system voltage prior to conversion, a capacitor bank is needed. | 2017-01-01 | Add a second 161/69 kV transformer at Wyoming - not viable due to increased cost to add a second transformer. | IA | IA | Planned | Other |  | Reliability | 69 | 69 | 0 | 0 | 1 |  | Amber Creamery Capacitor | ITC Midwest | Bottom-Up | Submitted for Recommendation
9672 | 2015-09-09 | A in MTEP16 |  | West | ITCM | 76th AVE SW Substation | ITC will need to construct a new four (4) terminal, four (4) breaker 69 kV substation southeast of the city of Cedar Rapids, Iowa in order to eliminate the coordination and system protection issues. The existing PCI – Tharp 69 kV transmission line will need to be tapped and re-routed into the new substation. The existing Prairie Creek Ckt. 0210 will need to be re-routed and terminated into the new substation when the area is converted as well. A 13.2 MVAR capacity bank will be installed at the new substation to provide voltage support for the area. | 2019-12-31 | 2019-12-31 | 4056304 | The 34.5 kV lines southeast of the Cedar Rapids, IA area are heavily loaded and in poor condition and are currently scheduled to be rebuilt to 69 kV standards to create a more efficient and reliable system. The conversion from 34.5 kV to 69 kV will drive the need for upgrades that will help coordination and eliminate system protection issues in the area. Additional voltage support is also required in the area to mitigate low voltage during expected and expected contingencies of the surrounding transmission system. | 2018-12-31 | Leave system as is. This option is not considered acceptable due to the coordination and system protection issues that the 34.5 to 69 kV conversion creates in the area. | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 0 | 4 |  | 76th AVE SW | ITC Midwest | Bottom-Up | Submitted for Recommendation
9706 | 2015-09-10 | A in MTEP16 |  | West | ITCM | Huntley 69 kV Maintenance | Relocate the 161/69 kV T1 transformer and replace the 161/69 kV T2 transformer with the Adams 161/69 kV 75 MVA transformer and the 69 kV breakers at the new proposed Huntley substation. | 2016-12-31 | 2016-12-31 | 9055247 | The current 69 kV breakers at the Winnebago Jct. substation are General Electric 69 kV breakers manufactured in 1950s or 1960s and are currently having maintenance issues. The current Control House building, controls, cable and relaying are 1954 vintage and are in need of upgrading. The 161/69 kV T2 transformer was built in 1956 and the LTC is currently broken and not repairable. The T2 transformer is also a 30 MVA rated transformer and overloads when the 161/69 kV T1 transformer is out of service during high loading conditions. | 2016-12-31 |  | MN | IA | Planned | Other |  | Reliability | 161 | 69 | 0 | 0 | 7 |  | Huntley 69 kV Maintenance | ITC Midwest | Bottom-Up | Submitted for Recommendation
9711 | 2015-10-19 | A in MTEP16 |  | West | ITCM | Traer 161 kV Ring Bus | Convert the Traer 161 kV to a ring bus design. | 2017-12-31 | 2017-12-31 | 5065882 | At Traer substation there are no 161 kV line breakers. Operations on the 161 kV line between Abbott substation and Dysart substation results in outages to the customers served from Traer if the 69 kV and 34.5 kV lines are operating radial. | 2018-12-31 |  | IA | IA | Planned | BaseRel |  |  | 161 | 161 | 0 | 0 | 3 |  | Traer 161 kV Ring Bus | ITC Midwest | Bottom-Up | Submitted for Recommendation
9712 | 2015-09-10 | A in MTEP16 |  | West | ITCM | BGS Substation Upgrades | Modify the Burlington Generating Station’s substation for increased reliability and to accommodate the required NERC PRC-005 maintenance testing of the BGS relaying schemes. Replace 161 kV circuit switcher 1272 with a breaker to isolate the BGS - Denmark #2 161 kV line from 161/69 kV T2 transformer. The 69 kV motor-operated switches will be replaced with 69 kV main circuit breakers to create separately relayed 161/69 kV transformer and 69 kV bus sections. Additional three-phase 161 kV voltage transformers will be added. A new control enclosure will be added outside the BGS power plant. All ITC relaying will be replaced and be installed in this new enclosure. The existing schemes in the BGS plant control room will be retired and removed. | 2017-06-01 | 2017-06-01 | 3114346 | At the Burlington Generating Station substation there are numerous protection and operational issues with the outdated design of the substation. Currently the 161/69 kV transformer T2 operates as part of the line for BGS - Denmark #2 161 kV line faults. There are 69 kV motor-operated switches on the low-side of the 161/69 kV transformers. The present substation equipment does not accommodate the required NERC PRC-005 maintenance testing of the BGS relaying schemes without extensive substation outages. |  |  | IA | IA | Planned | BaseRel |  |  | 161 | 69 | 0 | 0 | 1 |  |  | ITC Midwest | Bottom-Up | Submitted for Recommendation
9714 | 2015-09-11 | A in MTEP16 |  | West | ITCM | Doud-Lyon 34 to 69 kV Conv | Construct a new 69 kV breaker station near Lyon with 3 line terminals. The station should be laid out to accommodate a future additional breaker position for an Alliant Energy distribution transformer. Re-connect or extend 69 kV taps to the connected distribution substations and convert to 69 kV operation from the new station near Lyon to Doud. | 2019-12-31 | 2019-12-31 | 4638479 | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | 2018-12-31 |  | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 35.2 | 10 |  | Doud-Lyon 34 to 69 kV Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
9901 | 2015-11-18 | A in MTEP16 |  | West | ITCM | Mount Ayr 69 kV Substation Rebuild | Complete rebuild of the substation with all new equipment was proposed. Due to space limitations at the existing site, a new Kneedler (Mt. Ayr) 69kV breaker station will be constructed just north of the Mt. Ayr site. The existing 8.1MVAr cap will be replaced with a 3-stage 8.4MVAr (25.2MVAr total) capacitor bank at the Kneedler sub site. | 2018-12-31 | 2018-12-31 | 4944594 | Due to age and condition the 69 kv substation near Mt. Ayr, IA needs be to be rebuild. By rebuilding the substation ITC will not only improve reliability, but increase the overall ampacity of the substation. | 2018-12-31 | Leave as-is, but this is not a viable alternative due to age and condition issues with the existing substation. | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 0 | 3 |  | Mount Ayr 69 kV Sub Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9904 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Appanoose Co 161 kV Rebuild | ITC will replace it with a unit equipped with a Load Tap Changer (LTC). The 100 MVA (equipped with a LTC) 161:69kV transformer at Fernald will be relocated to Appanoose County after the MGS upgrades are completed. In addition, to increase reliability, ITC will rebuild the existing 161kV bus to a ring configuration. | 2019-12-31 | 2019-12-31 | 4944594 | Due to lack of voltage support in the area, ITC will move the existing 100 MVA 161-69kV transformer with a LTC from Fernald to Appanoose County. This unit was scheduled for retirement with the Marshalltown Gas Plant upgrades, but will be moved to Appanoose substation. Currently, Appanoose County only has one line breaker for the entire three terminal 161kV bus. To improve reliability the 161kV bus will be rebuild to a ring configuration. | 2019-12-31 | Install a 161kV line breaker to the existing straight bus, but a ring bus increases the reliability substantially. | IA | IA | Planned | BaseRel |  |  | 161 | 69 | 0 | 0 | 1 |  | Appanoose Co 161 kV Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9907 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Summit to Dovray 69 kV Rebuild | Phase 1: Rebuild ~12.9 miles of old line to new T2-4/0 ACSR | 2022-12-31 | 2022-12-31 | 9162091 | Due to age and condition this 69 kV circuit needs to be rebuild with T2-4/0 conductor. The existing 4/0 conductor has galloping issues and operates frequently. This is part one of a three part plan. | 2018-12-31 |  | MN | MN | Planned | Other |  | Condition | 69 | 69 | 0 | 12.89 | 1 |  | Summit to Dovray 69 kV Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9908 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Dovray to Fulda 69 kV Rebuild | Rebuild ~14.5 miles of old line to new T2-4/0 ACSR | 2023-12-31 | 2023-12-31 | 9410124 | Due to age and condition this 69 kV circuit needs to be rebuild with T2-4/0 conductor. The existing 4/0 conductor has galloping issues and operates frequently. This is part one of a three part plan. | 2019-12-31 |  | MN | MN | Planned | Other |  | Condition | 69 | 69 | 0 | 14.5 | 1 |  | Dovray to Fulda 69 kV Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9910 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Fulda to Heron Lake 69 kV Rebuild | Rebuild ~20.14 miles of old line to new T2-4/0 ACSR | 2024-12-31 | 2024-12-31 | 14976652 | Due to age and condition this 69 kV circuit needs to be rebuild with T2-4/0 conductor. The existing 4/0 conductor has galloping issues and operates frequently. This is part one of a three part plan. | 2020-12-31 |  | MN | MN | Planned | Other |  | Condition | 69 | 69 | 0 | 20.14 | 1 |  | Fulda to Heron Lake 69 kV Rebuild | ITC Midwest | Bottom-Up | Submitted for Recommendation
9937 | 2015-09-15 | A in MTEP16 |  | West | ITCM | J233-Network Upgrades | Replace existing 161/69 kV transformers with 150 MVA units at Fernald, Jasper, and Newton substations. Uprate the Marshalltown-Blairstown Junction 115 kV line to 90 MVA; Uprate the Jasper to Laurel161 kV to 361 MVA; remove sag limit from Jasper to Newton 161 kV line to allow operation at 276 MVA; Rebuild ITCM's portion of the Newton to Prairie City 69 kVwith T2-4/0 ACSR to allow operation at MEC's rating of 40 MVA | 2015-09-15 | 2017-03-30 | 17740415 | Upgrades required for the interconnection of project J233, a 635 MW combined cycle gas plant connecting to Marshalltown 161 kV | 2017-03-30 | Alternatives vetted through DPP August 2013 study and Restudy | IA | IA | Planned | GIP | Not Shared |  | 161 | 69 | 0 | 0 | 8 |  | J233 Network Upgrades | ITC Midwest | Externally Driven | Recommended
9939 | 2015-09-15 | A in MTEP16 |  | West | ITCM | H009-Jasper-Aurora 69 kV | Rebuild Jasper to Aurora Heights 69 kV with T2-477 ACSR | 2016-12-31 | 2016-12-31 | 3720000 | Required network Upgrade under GIA for project H009 | 2016-12-31 | Alternatives vetted through DPP August 2012 Restudy | IA | IA | Planned | GIP | Not Shared |  | 69 | 69 | 0 | 0 | 1 |  | H009-Jasper-Aurora 69 kV | ITC Midwest | Externally Driven | Recommended
9941 | 2015-09-15 | A in MTEP16 |  | West | ITCM | H021-Traer-Traer Tap 69 kV | Upgrade Traer to Trear Tap 69 kV | 2016-06-01 | 2016-06-01 | 293449 | Required Netowrk Upgraade under GIA for project H021 | 2016-06-01 | Alternativives vetted through DPP August 2012 Study | IA | IA | Planned | GIP | Not Shared |  | 69 | 69 | 0 | 0 | 1 |  | H021-Traer-Traer Tap 69 kV | ITC Midwest | Externally Driven | Recommended
9985 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Newhall-Williamsburg 161 kV Rebuild | Rebuild Williamsburg 115kV tap to 161kV | 2018-12-31 | 2018-12-31 | 40174153 | Due to age and condition of the Williamsburg 115kV tap needs to be rebuilt. ITC will rebuild the tap to 161kV T2-795 ACSR. The rebuild provides additional reliability to the Marshalltown-Cedar Rapids conversion. | 2018-12-31 | Rebuild the 115kV Williamsburg to Morgan Valley/Beverly | IA | IA | Planned | Other |  | Condition | 161 | 161 | 3 | 23 | 1 |  | Newhall-Williamsburg 161 kV | ITC Midwest | Bottom-Up | Submitted for Recommendation
9988 | 2015-09-15 | A in MTEP16 |  | West | ITCM | Newhall 161 kV Breaker Station | Construct a new 3 position 161kV breaker station | 2018-12-31 | 2018-12-31 | 8090882 | Needed to support the rebuild of the Williamsburg to Newhall 161kV line. | 2018-12-31 | Construct Morgan Valley 161kV Substation/Add terminal at Beverly 161kV substation | IA | IA | Planned | Other |  | Condition | 161 | 161 | 0 | 0 | 2 |  | Newhall 161 kV Breaker Station | ITC Midwest | Bottom-Up | Submitted for Recommendation
10022 | 2015-09-15 | A in MTEP16 |  | West | ITCM | PCI-Mt.Vernon-Lisbon-76th AVE Conv | ITC will be converting the PCI to Mt. Vernon to Lisbon North to 76th Ave. substation from 34.5 kV operation to 69 kV operation. To accommodate the conversion, a 69 kV breaker and associated equipment will be installed at the PCI substation, two (2) 69 kV breakers and associated equipment will be installed at the Lisbon North substation, approximately 0.6 mile of new 69 kV transmission line will be constructed to complete the PCI to 76th Ave circuit and OPGW will need to be installed. | 2019-12-31 | 2019-12-31 | 5793932 | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | 2018-12-31 |  | IA | IA | Planned | Other |  | Condition | 69 | 69 | 0 | 0 | 5 |  | PCI-Mt.Vernon-Lisbon-76thAVE Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
10023 | 2015-09-17 | A in MTEP16 |  | West | ITCM | ITC Midwest Asset Replacement Program | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | 2017-12-31 | 2019-12-31 | 111600000 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | 2019-12-31 |  | IA,MN,IL | IA,MN,IL | Planned | Other |  | Condition | 345 | 69 | 0 | 0 | 3 |  | ITCM Asset Blanket | ITC Midwest | Bottom-Up | Submitted for Recommendation
10024 | 2015-09-15 | A in MTEP16 |  | West | ITCM | ITCM Customer Interconnects with short lead time | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | 2019-12-31 | 2019-12-31 | 2000000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | 2019-12-31 |  | IA,MN,IL | IA,MN,IL | Planned | Other |  | Distribution | 345 | 69 | 0 | 0 | 1 |  | Cust Interconnet Blanket | ITC Midwest | Bottom-Up | Submitted for Recommendation
10268 | 2015-10-28 | A in MTEP16 |  | West | ITCM | Dubuque 8th Street Distribution Transformer Upgrades | This project consists of the ITC work required to allow for the replacement of the two 69/distribution transformers at the 8th Street substation. This project will move the Alliant distribution transformer T-225 position to the existing Sandridge (bkr 253) position & move the ITC owned Sandridge terminal equipment to the former T-255 (bkr 252) position. Alliant will move the T-140 (bkr 257) position to the former North Clinton (bkr 256) position. This project will also require relay upgrades. In addition, the removal of a guyed structure and replace with a new self-supported structure within the substation will be required. | 2017-04-30 | 2017-04-30 | 1603393 | Upgrades are needed to allow Alliant Energy to replace the 69kV/distribution transformers at the 8th Street substation. | 2017-05-31 |  | IA | IA | Planned | Other |  | Reliability | 69 | 69 | 0 | 0 | 3 |  | DBQ 8th ST dist TRFs | ITC Midwest | Bottom-Up | Submitted for Recommendation
10269 | 2015-10-30 | A in MTEP16 |  | West | ITCM | Lore-Hickory Creek 161kV Rebuild | Rebuild 6.81 miles of the Lore-Hiclory Creek 161kV line and upgrade the Lore 161kV terminal. | 2017-12-31 | 2017-12-31 | 12700847 | Needed to maintain system reliability in the Dubuque/eastern Iowa area with area generatin offline. The Lore-Hickory Creek 161 kV line will overload for the 161kV bus tie breaker failure at Salem and other N-2 contingencies. | 2017-12-31 |  | IA | IA | Planned | BaseRel |  |  | 161 | 161 | 0 | 0 | 3 |  | Lore-Hickory 161 | ITC Midwest | Bottom-Up | Submitted for Recommendation
10303 | 2015-11-05 | A in MTEP16 |  | West | ITCM | Willaimsburg 161kV Temp Conversion | To provide a reliable conversion to 69kV the 34.5kV will need temporary configurations to provide a reliable transition. The Williamsburg 115kV high side will be converted to 161kV. The two aging and miss-matched 115/34.5kV transformers will be replaced with a newer and larger 161/36kV transformer from the Hiawatha Substation. This will provide an increased level of reliability to Williamsburg by serving the high-side from a newly rebuilt and shorter 161kV line compared to an older and longer 115kV line. | 2017-12-30 | 2017-12-31 | 1204368 | The long term plan is to eliminate the 34.5kV system which is heavily loaded and in poor condition while creating and/or utilizing existing higher voltage (69kV, 115kV, and 161kV) infrastructure to adequately serve the Marshalltown – Parnell - Cedar Rapids area. Part of the long term plan is to build/rebuild the Parnell-Newhall 161kV. | 2017-12-30 |  | IA | IA | Planned | Other |  | Reliability | 161 | 34 | 0 | 0 | 2 |  | Willaimsburg 161kV Temp Conv | ITC Midwest | Bottom-Up | Submitted for Recommendation
11163 | 2016-05-02 | A in MTEP16 |  | West | ITCM | Devils Creek | 69 kV customer interconnection near Ft. Madison, IA. Build a new Devils Creek 69kV distributions substation. | 2017-12-31 | 2017-12-31 | 2026223 | IPL is rebuilding an existing substation in place and consolidating area load, to support their project ITCM will from an in and out configuration and install two line breakers at the new substation. | 2017-12-31 | Tap the load off of the existing line without installing bus and breakers - not viable due to the proposed size of the load, and the resulting decreased reliability. | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 4 |  | Devils Creek | ITC Midwest | Bottom-Up | Submitted for Recommendation
11164 | 2016-05-02 | A in MTEP16 |  | West | ITCM | Oelwein Hub Distribution Sub | ITCM will form an in and out configuration and install two line breakers at the new substation. | 2017-04-30 | 2017-04-30 | 6317468 | IPL is connecting a new customer load South of Oelwein, IA. To support the interconnection ITCM will form an in and out configuration and install two line breakers at the new substation. | 2017-12-31 | Tap the load off of the existing line without installing bus and breakers - not viable due to the proposed size of the load, and the resulting decreased reliability. | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 1.42 | 4 |  | Oelwein Hub | ITC Midwest | Bottom-Up | Submitted for Recommendation
8821 | 2015-08-21 | A in MTEP16 |  | West | LAFA | Northeast to Peck | 69kv line connecting Northeast station to Peck station. | 2019-12-31 | 2019-12-31 | 4230000 | This is part 2 of a 2 part project. The first project was a new 230-69 autotransformer located at Pont Des Mouton station and a new 69kv line from Pont Des Mouton to a new Northeast station. Part 2 of this project will be a 69kv transmission line from the Northeast station to Peck station. This new path will alleviate a contingent loading on the Bonin 138-69 transformers. | 2019-12-31 |  | LA | LA | Proposed | Other |  | Distribution | 69 | 0 | 0 | 0 | 1 |  |  | Lafayette Utilities System | Bottom-Up | Submitted for Recommendation
4140 | 2015-06-10 | A in MTEP16 |  | West | MDU | Bowdle Jct | Build a new Bowdle Jct to replace old Bowdle substation | 2017-06-30 | 2017-06-30 | 5500000 | The existing Bowdle Jct is in a low lying area with potential for water problems | 2016-12-31 | N/A | SD | SD | Planned | Other |  | Reliability | 115 | 41.6 | 0 | 0 | 1 | Y | Bowdle | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Recommendation
9120 | 2015-07-13 | A in MTEP16 |  | West | MDU | Leola | A new 115 kV transmission line from the Ellendale Jct. Substation to a new Leola Jct. 115/41.6 Substation. The new Leola Jct. substation will connect to the existing Ellendale-Bowdle 41.6 kV line. | 2017-10-31 | 2017-10-31 | 12835000 | Low voltages and thermal overloads on 41.6 kV system for various outage conditions | 2017-12-31 |  | SD,ND | SD | Planned | Other |  | Reliability | 115 | 41.6 | 45 | 0 | 2 |  |  | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Recommendation
9121 | 2015-06-10 | A in MTEP16 |  | West | MDU | Heskett-Mandan 115 Upgrade | Replace limiting switches in the Heskett substation on the Mandan 115 kV line. | 2016-12-31 | 2016-12-31 | 125000 | Overload of Heskett-Mandan 115 kV line for loss of Heskett-NE Bismarck 115 kV line during summer peak conditions | 2017-06-01 |  | ND | ND | Planned | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  |  | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Recommendation
11403 | 2016-06-20 | A in MTEP16 |  | West | MDU | TSR F109/A634 | Reconductor Coyote-Beulah 115 kV line | 2015-12-31 | 2015-12-31 | 350000 | Network upgrade for TSR F109/A634 | 2015-12-31 |  | ND | ND | M5_In Service | TDSP |  |  | 115 | 0 | 0 | 4.3 | 1 |  |  | Montana-Dakota Utilities Company | Externally Driven | Recommended
8108 | 2015-09-15 | A in MTEP16 | B>A | West | MEC | Sub 73 - Dupont 69 kV Line Upgrade | Replace structures to allow a higher operating temperature for the line. | 2017-06-01 | 2017-06-01 | 40000 | N-1-1 thermal overloads in MTEP14 models | 2017-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0.63 | 1 | NT |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
8110 | 2015-09-15 | A in MTEP16 | B>A | West | MEC | Sub 73 - Elvira Tap 69 kV line upgrade | Replace structures on the Sub 73-Elvira 69 kV line to allow a higher operating temperature. | 2017-06-01 | 2017-06-01 | 50000 | N-1-1 thermal overloads in MTEP14 models | 2017-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 1.95 | 1 | NT |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
8112 | 2015-09-15 | A in MTEP16 | B>A | West | MEC | Buffalo Bill Tap - Elvira Tap 69 kV line upgrade | Replace structures to allow a higher conductor operating temperature. | 2017-06-01 | 2017-06-01 | 25000 | N-1-1 thermal overloads in MTEP14 models. | 2017-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 6.36 | 1 | NT | G7055 | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9947 | 2015-09-15 | A in MTEP16 |  | West | MEC | Polk City Substation and Lines | Build a new 33 MVA 161-13 kV distribution substation near Polk City, Iowa with 161 kV line taps connecting to the Bittersweet-NE Ankeny 161 kV line. | 2020-06-01 | 2020-06-01 | 7000000 | Serve growing distribution load. | 2018-06-01 |  | IA | IA | Planned | Other |  | Distribution | 161 | 13 | 7 | 0 | 3 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9973 | 2016-06-07 | A in MTEP16 |  | West | MEC | Manawa Second Transformer | Add a second 33 MVA 161-13 kV transformer at the Manawa Substation. | 2017-10-01 | 2017-10-01 | 1100000 | Serve growing 13 kV distribution load in the area. | 2017-10-01 |  | IA | IA | Planned | Other |  | Distribution | 161 | 13 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9976 | 2016-06-07 | A in MTEP16 |  | West | MEC | Avoca transformer 69 kV circuit breaker | Add a 69 kV circuit breaker on the low side of Avoca 161-69 kV transformer 8T1. | 2016-12-01 | 2016-12-01 | 415000 | Eliminates additional 69 kV equipment from tripping for faults on 161-69 kV transformer 8T1 and mitigate post-contingent low voltage levels. | 2016-12-01 |  | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9980 | 2015-09-15 | A in MTEP16 |  | West | MEC | Teakwood 34.5 kV Reactors | Add two 10 MVAr 34.5 kV reactors at Teakwood Substation. | 2016-10-01 | 2016-10-01 | 850000 | Mitigates post contingent high voltage at Teakwood Substation. | 2016-06-01 |  | IA | IA | Planned | Other |  | Reliability | 34.5 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9981 | 2015-09-15 | A in MTEP16 |  | West | MEC | Sub 701-Honey Creek 69 kV Line | Rebuild the Sub 701-Honey Creek 69 kV line. | 2017-06-01 | 2017-06-01 | 3250000 | Mitigates single & n-1-1 contingency line overloads by rebuilding the line & replacing limiting terminal equipment. | 2017-06-01 |  | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 10.2 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9987 | 2015-09-15 | A in MTEP16 |  | West | MEC | Johnston 161-13 kV Substation | Construct a new Johnston 33 MVA 161-13 kV distribution substation. | 2016-11-30 | 2016-11-30 | 2130000 | Serve growing distribution load. | 2016-11-30 |  | IA | IA | Planned | Other |  | Distribution | 161 | 13 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9992 | 2015-09-15 | A in MTEP16 |  | West | MEC | Lake Cornelia-Coulter 69 kV Upgrade | Replace limiting structures on the Lake Cornelia-Coulter 69 kV line to increase line rating. | 2016-07-01 | 2016-07-01 | 59000 | Mitigates overloads for n-1-1 contingencies. | 2016-08-01 |  | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9993 | 2015-09-15 | A in MTEP16 |  | West | MEC | Humboldt East-Thor 69 kV Upgrade | Upgrade the Humboldt East-Thor 69 kV line by replacing limiting structures. | 2016-04-13 | 2016-04-13 | 61000 | Mitigates overloads for n-1-1 contingencies | 2016-08-01 |  | IA | IA | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
9996 | 2016-06-07 | A in MTEP16 |  | West | MEC | Eagle Grove Second 69-13 kV transformer | Install a second 69-13 kV Transformer & 69 kV bus tie breaker at the Eagle Grove Substation | 2016-12-09 | 2016-12-09 | 2440000 | Additional transformer capacity is needed to serve increased load. | 2016-12-09 |  | IA | IA | Planned | Other |  | Distribution | 69 | 13 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10002 | 2015-09-15 | A in MTEP16 |  | West | MEC | Sub 39 second 161-69 kV transformer | Install a second 125 MVA 161-69 kV transformer at Sub 39. | 2018-06-01 | 2018-06-01 | 960000 | Driven by n-1-1 contingencies. | 2018-06-01 |  | IA | IA | Planned | Other |  | Reliability | 161 | 69 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10004 | 2015-09-16 | A in MTEP16 |  | West | MEC | Sub 18 replace transformer 8T3 | Replace 161-69 kV transformer 8T3 at Sub 18 with a 167 MVA unit. | 2017-06-01 | 2017-06-01 | 1080000 | Driven by n-1-1 contingencies. | 2017-06-01 |  | IA | IA | Planned | Other |  | Reliability | 161 | 69 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10005 | 2015-09-18 | A in MTEP16 |  | West | MEC | Replace 161 kV Circuit Breaker at Plymouth | Replace 161 kV circuit breaker 9610 at Plymouth Substation | 2015-12-31 | 2015-12-31 | 264000 | Upgrade needed to have adequate interrupting capability. | 2015-12-31 |  | IA | IA | Planned | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10006 | 2015-09-18 | A in MTEP16 |  | West | MEC | Sycamore Substation: replace three 161 kVK circuit breakers | Replace 161 kV circuit breakers AG805, AG812 and AG816 at Sycamore Substation. | 2016-12-31 | 2016-12-31 | 685000 | New circuit breakers needed to maintain adequate current interrupting capability. | 2016-12-31 |  | IA | IA | Planned | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10009 | 2015-09-18 | A in MTEP16 |  | West | MEC | Bondurant: Replace 161 kV circuit breaker | Replace 161 kV circuit breaker AH810 at Bondurant Substation. | 2016-10-31 | 2016-10-31 | 325000 | Replace circuit breaker to maintain adequate current interrupting capability. | 2016-06-01 |  | IA | IA | Planned | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10503 | 2015-12-21 | A in MTEP16 |  | West | MEC | Tate & Lyle Bus Tie Breaker | Add a 161 kV bus tie circuit breaker at Tate & Lyle Substaiton | 2016-07-21 | 2016-07-21 | 443000 | Project will increase system reliability during bus faults at the substation. | 2016-06-01 |  | IA | IA | Planned | BaseRel |  | Distribution | 161 | 0 | 0 | 0 | 1 | Y | Q1138 | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10663 | 2016-01-29 | A in MTEP16 |  | West | MEC | Willow Creek Substation Expansion | Expand the Willow Creek Substation 161 kV bus to accommodate a new 50 MVA 161-13 kV transformer. Add three new 161 kV circuit breakers and convert the substation to a breaker and one-half configuration. | 2016-12-31 | 2016-12-31 | 120000 | Load growth at this substation is projected to reach 38.6 MW by October 1, 2017. | 2016-12-31 |  | IA | IA | Planned | Other |  | Distribution | 161 | 13.2 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10664 | 2016-01-29 | A in MTEP16 |  | West | MEC | 34th Avenue 3rd Transformer | Install a third 161-13 kV 62 MVA transformer and associated equipment at the 34th Ave. NW Substation. | 2016-12-01 | 2016-12-01 | 90000 | The load served from the 34th Ave. NW Substation is projected to reach 70 MW by October 1, 2017. | 2016-12-01 |  | IA | IA | Planned | Other |  | Distribution | 161 | 13.2 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10803 | 2016-02-29 | A in MTEP16 |  | West | MEC | Sub J Iowa City Reduce Capactor Bank Size | Reduce the size of the existing 161 kV capacitor bank at Sub J Iowa City, from 50.4 MVAR to 37.8 MVAR. The capacitor bank relaying will also be replaced at this time. | 2016-12-01 | 2016-12-01 | 300000 | Switching the existing 161 kV, 50.4 MVAR capacitor bank at Sub J in Iowa City can cause bus voltages to exceed 105% of nominal, which is a violation of MidAmerican Energy’s local area reliability planning criteria. | 2016-12-01 | The following alternative project was considered but not selected: Install a ‘reverse power’ relay on the Sub J 161-69 kV transformer to trip the transformer for sustained power flows from the 69 kV to the 161 kV bus above a certain set point. | IA | IA | Planned | BaseRel |  |  | 161 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Submitted for Recommendation
10867 | 2016-03-08 | A in MTEP16 |  | West | MEC | J285 Interconnection Facilities | Add one 345 kV circuit breaker position at Obrien County Substation 345 kV ring bus for the J285 generator interconnection. | 2016-08-15 | 2016-08-15 | 3000000 | Facilities required to interconnect J285 generator project. | 2016-08-15 |  | IA | IA | Under Construction | GIP | Shared |  | 345 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Externally Driven | Recommended
10868 | 2016-03-17 | A in MTEP16 |  | West | MEC | J411 Interconnection Facilities (Ida Co. Substation) | Construct a new three-terminal 345 kV ring bus substation (Ida County Substation), bisecting the Raun-Lehigh 345 kV line for the J411 generator interconnection. Install new transposition structures for the Raun-Ida County and Ida County-Lehigh 345 kV lines. ITC Midwest will have an ownership share of the network transmission facilities. | 2016-07-15 | 2016-07-15 | 5750000 | Facilities required to interconnect the J411 generation project. | 2016-07-15 |  | IA | IA | Under Construction | GIP | Shared |  | 345 | 0 | 0 | 0 | 1 |  |  | MidAmerican Energy Company | Externally Driven | Recommended
11103 | 2016-05-12 | A in MTEP16 |  | West | MEC | Black Hawk: Install 2-69 kV Cap Banks | Add two 69 kV, 15 MVAR capacitor banks at Black Hawk Substation. | 2016-11-15 | 2016-11-15 | 1180000 | Generator interconnection network upgrades. | 2016-12-31 |  | IA | IA | Under Construction | GIP | Not Shared |  | 69 | 0 | 0 | 0 | 1 |  | T90D4 | MidAmerican Energy Company | Externally Driven | Recommended
11143 | 2016-06-07 | A in MTEP16 |  | West | MEC | Creston-Macksburg 161 kV Uprate | Structure replacements. | 2016-12-01 | 2016-12-01 | 175000 | J274 network upgrades | 2016-12-01 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90D9 | MidAmerican Energy Company | Externally Driven | Recommended
11144 | 2016-04-27 | A in MTEP16 |  | West | MEC | Sub T(FD): Replace 161 kV Sw 11-817 | Replace 161 kV Switch 11-817 | 2016-06-24 | 2016-06-24 | 88000 | R42 network upgrades | 2016-06-24 |  | IA | IA | Under Construction | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90DK | MidAmerican Energy Company | Externally Driven | Recommended
11145 | 2016-06-07 | A in MTEP16 |  | West | MEC | Sub T FD-Boone Jct 161 Line Uprate | structure replacements | 2016-06-30 | 2016-06-30 | 173000 | R42 network upgrades | 2016-06-30 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T905K | MidAmerican Energy Company | Externally Driven | Recommended
11146 | 2016-04-27 | A in MTEP16 |  | West | MEC | Clarinda-Brooks 161 kV Uprate | structure replacements | 2017-06-01 | 2017-06-01 | 200000 | J343 network upgrades | 2017-06-01 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90LA | MidAmerican Energy Company | Externally Driven | Recommended
11283 | 2016-05-25 | A in MTEP16 |  | West | MEC | Clarinda-Maryville 161 kV Uprate | Replace three structures. | 2017-06-01 | 2017-06-01 | 100100 | Network Upgrades for J343 Adams County Wind. | 2017-06-01 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90L8 | MidAmerican Energy Company | Externally Driven | Recommended
11284 | 2016-05-25 | A in MTEP16 |  | West | MEC | Clarinda Substation: Replace 161 kV Switch 803L | At Clarinda Substation, on the line terminal to Maryville, install a new 161 kV line disconnect switch, replace associated line drops and jumpers, and remove the existing switch. | 2017-06-01 | 2017-06-01 | 80500 | Network Upgrades for J343 Adams County Wind. | 2017-06-01 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90KU | MidAmerican Energy Company | Externally Driven | Recommended
11285 | 2016-05-25 | A in MTEP16 |  | West | MEC | Beacon 161 kV Line Drops, Poweshiek | Replace line drops at Beacon Substation on the Beacon–Poweshiek 161 kV line terminal. | 2017-09-01 | 2017-09-01 | 25000 | Non-Stand Alone Network Upgrade for the J344 wind interconnection request. | 2017-09-01 |  | IA | IA | Planned | GIP | Not Shared |  | 161 | 0 | 0 | 0 | 1 |  | T90M4 | MidAmerican Energy Company | Externally Driven | Recommended
7910 | 2015-09-04 | A in MTEP16 | B>A | West | MP | 5 Line Upgrade | Increase capacity of Brainerd - Mud Lake 115 kV Line | 2019-11-01 | 2019-11-01 | 1900000 | Post-contingent loading for loss of Riverton - Mud Lake 230 kV Line | 2019-11-01 |  | MN | MN | Planned | BaseRel |  |  | 115 | 0 | 0 | 4.41 | 1 | Y | 5 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
7996 | 2015-09-11 | A in MTEP16 | B>A | West | MP | 15 Line Upgrade | Rebuild & reconductor Fond Du Lac - Hibbard 115 kV Line | 2017-12-31 | 2017-12-31 | 5500000 | Age & condition Post-contingent loading |  |  | MN | MN | Proposed | BaseRel |  |  | 115 | 0 | 0 | 11.3 | 1 | Y | 15 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
7997 | 2015-09-04 | A in MTEP16 | B>A | West | MP | 15th Avenue West Modernization | Rebuild & modernize existing 15th Avenue West Substation, including new 14 kV switchgear, one new 115/14 kV transformer, replace 3 115 kV breakers and other 115 kV equipiment, and miscellaneous site improvements | 2018-05-01 | 2018-12-31 | 10000000 | Age & condition Reliability | 2018-12-31 |  | MN | MN | Planned | Other |  | Condition | 115 | 13.8 | 0 | 0 | 6 | Y | 15th Ave West | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9064 | 2015-09-08 | A in MTEP16 | B>A | West | MP | Arrowhead 115 kV Bus Reconfiguration | Reconfigure Arrowhead 115 kV bus to eliminated 115 MW breaker failure contingency. Cannot have Arrowhead - Colbyville & Arrowhead - Haines Road on adjacent buses | 2019-12-31 | 2019-12-31 | 1500000 | Reliability - Arrowhead 115MW breaker failure or simultaneous outage of Arrowhead - Haines Road and Arrowhead - Colbyville causes voltage violations | 2019-12-31 | None | MN | MN | Conceptual | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | Arrowhead Bus Reconfiguration | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9622 | 2015-09-04 | A in MTEP16 |  | West | MP | 83 Line Upgrade | Replace limiting elements at Boswell & Blackberry to restore 100C rating | 2019-06-01 | 2019-06-01 | 500000 | Restore capacity on generator outlet line (line was derated after NERC-mandated equipment audit) | 2019-06-01 |  | MN | MN | Proposed | Other |  | Reliability | 230 | 0 | 0 | 0 | 2 |  | 83 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9623 | 2015-09-04 | A in MTEP16 |  | West | MP | 95 Line Upgrade | Replace limiting elements at Boswell & Blackberry to restore 100C rating | 2019-06-01 | 2019-06-01 | 500000 | Restore capacity on generator outlet (line was derated after NERC-mandated equipment audit) | 2019-06-01 |  | MN | MN | Proposed | Other |  | Reliability | 230 | 0 | 0 | 0 | 2 |  | 95 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9624 | 2015-09-04 | A in MTEP16 |  | West | MP | Bear Creek 69/46 kV Transformer | Install 69/46 kV transformer at Great River Energy's existing Bear Creek Substation and remove existing Sandstone 69/46 kV distribution station | 2017-12-31 | 2017-12-31 | 2000000 | Age & condition of Sandstone distribution station | 2017-12-31 |  | MN | MN | Planned | Other |  | Condition | 69 | 46 | 0 | 0 | 1 |  | Bear Creek Transformer | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9625 | 2015-09-04 | A in MTEP16 |  | West | MP | Nemadji 115 kV Project | New switching station in Gary - Stinson 115 kV Line near Enbridge's Superior Terminal; 115 kV line development around the Superior Terminal | 2014-12-31 | 2017-12-31 | 8690000 | System Reliability - reduce exposure to large industrial customer; reduce system exposure to customer-owned equipment | 2017-12-31 |  | WI | WI | Planned | Other |  | Reliability | 115 | 0 | 2.84 | 0 | 9 |  | Nemadji | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
10284 | 2015-10-30 | A in MTEP16 |  | West | MP | 28 Line Upgrade | Increase emergency rating of Boswell - Canisteo 115 kV Line to at least 150 MVA | 2017-06-01 | 2017-06-01 | 0 | Post-contingent flow on Boswell - Canisteo 115 kV Line exceeds the line's present summer emergency rating (132 MVA) for loss of the double circuited segment of the Boswell - Blandin & Boswell - Grand Rapids 115 kV lines. | 2017-05-01 |  | MN | MN | Planned | BaseRel |  |  | 115 | 0 | 0 | 0 | 2 |  | 28 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
10383 | 2015-12-02 | A in MTEP16 |  | West | MP | Laskin-Tac Harbor Voltage Conversion | Convert Laskin - Tac Harbor 138 kV system to 115 kV and add a 15 MVAr capacitor bank at Dunka Road; coordinated with the Hoyt Lakes Substation Modernization (Project #4426) and Dunka Road Substation (Project #2761) | 2017-07-01 | 2017-12-31 | 2484000 | Remove single points of failure - aging 138/115 kV transformers at Tac Harbor and Laskin with no viable spare. Avoid purchase of new 138/115 kV transformers. Add voltage support in absence of Tac Harbor generation | 2017-12-31 |  | MN | MN | Planned | Other |  | Condition | 115 | 13.8 | 0 | 0 | 7 |  | Voltage Conversion | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Recommendation
9582 | 2016-03-01 | A in MTEP16 |  | West | MPC | Jamestown-Buffalo 345 kV Line Uprate | Increase clearance of Jamestown-Buffalo line to 70 deg C by fixing a few limiting spans. Increase rating to at least 842 MVA on Jamestown-Buffalo. | 2016-11-30 | 2016-11-30 | 130000 | Mitigate interconnection and delivery impacts of a generator interconnection. | 2016-11-30 |  | ND | ND | Planned |  |  |  | 345 | 0 | 0 | 56.16 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9645 | 2015-09-08 | A in MTEP16 |  | West | MPC | Center-Sq Butte 230 kV Line Uprate | Reconductor of Center-Square Butte line to 959.6 22/7 Suwannee/TW (110 deg C), and uprate bus at Center to increase facility rating to 481 MVA. | 2016-08-31 | 2016-08-31 | 1000000 | Mitigate delivery impacts of a generator interconnection. | 2016-08-31 |  | ND | ND | M5_In Service |  |  |  | 230 | 0 | 0 | 1.91 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9648 | 2016-03-01 | A in MTEP16 |  | West | MPC | Pillsbury-Maple Rv 230 kV Line Uprate | Re-tap CTs on Maple River 230 kV breakers to increase rating of Pillsbury line to 478 MVA. | 2019-12-31 | 2019-12-31 | 9000 | Mitigate interconnection impacts of a generator interconnection. | 2019-12-31 |  | ND | ND | Planned |  |  |  | 230 | 0 | 0 | 61.05 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9649 | 2016-05-25 | A in MTEP16 |  | West | MPC | Clearbrook-Clearbrook West 115 kV Line | Add a new Clearbrook area line for serving a new load. | 2018-10-01 | 2018-10-01 | 4000000 | A new load is driving the need for a source to the area. | 2018-10-01 |  | MN | MN | Planned |  |  |  | 115 | 0 | 5.5 | 0 | 2 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9650 | 2015-12-11 | A in MTEP16 |  | West | MPC | Maple Rv-Frontier 69 kV Conversion to 115 kV | Phase 1 will rebuild an existing 69 kV line to accommodate a 69 kV line and 115 kV line from Stanley extending north to a new Veterans Blvd substation. The new line will initially operate at 69 kV (12/31/2015). It will go into 115 kV service thereafter. Phase 2 will rebuild an existing 69 kV line to accommodate a 69 kV line and 115 kV line from Maple River extending south to the Veterans Blvd substation. A 115 kV bay will be established at Frontier, and the Veterans Blvd-Frontier line and Veterans Blvd sub will be converted to 115 kV. The new Maple River-Veterans Blvd line will either be operated at 69 kV temporarily or be double circuited with dual 115/69 kV operation.Phase 3 will convert the remaining substations along the new Maple River-Veterans Blvd-Frontier line to 115 kV operation. | 2017-01-31 | 2020-12-31 | 38200000 | Load growth in the Fargo area is driving the need for expansion of the existing 69 kV system. Phase 1 will bring a new source to the distribution system and transfer some load to Frontier. Phase 2 will complete the 115 kV line between Maple River and Frontier and transfer some load off the 69 kV system. Phase 3 will finish converting the 69 kV distribution sources along the Maple River-Veterans Blvd-Frontier line to 115 kV high side service, including the addition of high side breaker protection for looped service at some locations. | 2020-12-31 |  | ND | ND | Planned |  |  |  | 230 | 115 | 0 | 11.5 | 9 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9651 | 2016-06-28 | A in MTEP16 |  | West | MPC | Moranville Transformer Replacement | Replace two Moranville transformers (1 x 230/115 kV, 1 x 115/69 kV) with a new 230/69 kV transformer. Two 230 kV breakers and a 69 kV breaker are also included. | 2017-12-31 | 2017-12-31 | 2500000 | Existing transformer taps do not allow for parallel operation of the existing transformers. Thermal limits are being approached as well. A new transformer will increase load serving capability, and existing transformation will be a sufficient backup. | 2017-12-31 |  | MN | MN | Planned |  |  |  | 230 | 69 | 0 | 0 | 3 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9652 | 2016-06-28 | A in MTEP16 |  | West | MPC | Ulrich Transformer Replacement | Increase the capacity of the existing Ulrich transformer. | 2018-12-31 | 2018-12-31 | 2500000 | The capacity of the existing Ulrich transformer is reaching its limit and needs to be replaced. Capacitors are needed to support load alternate source configurations. | 2018-12-31 |  | MN | MN | Planned |  |  |  | 115 | 69 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9653 | 2015-09-08 | A in MTEP16 |  | West | MPC | Alvarado Switch Replacement | Replace limiting switch for capacity increase. | 2015-12-31 | 2015-12-31 | 400000 | Replace limiting switch for capacity increase. | 2015-12-31 |  | MN | MN | M5_In Service |  |  |  | 115 | 0 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9654 | 2015-09-08 | A in MTEP16 |  | West | MPC | Center Breaker Replacement | Replace aging breakers. | 2015-10-31 | 2015-10-31 | 1000000 | Replace aging breakers with new, faster clearing breakers. | 2015-10-31 |  | ND | ND | M5_In Service |  |  |  | 230 | 0 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
9656 | 2016-06-28 | A in MTEP16 |  | West | MPC | Fossum Substation Conversion | Rebuild the existing 69 kV line to 115 kV from Prairie to the Fossum load. | 2019-12-31 | 2019-12-31 | 2000000 | To off-load the Prairie 115/69 kV transformers. | 2019-12-31 |  | ND | ND | Planned |  |  |  | 115 | 0 | 0 | 0.6 | 2 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
11263 | 2016-05-23 | A in MTEP16 |  | West | MPC | Itasca-MPL Laporte 115 kV Line | Add a new Itasca area line for serving a new load. | 2017-10-01 | 2017-10-01 | 7170000 | A new load is driving the need for a source to the area. | 2017-10-01 |  | MN | MN | Planned |  |  |  | 115 | 0 | 18 | 0 | 4 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
11286 | 2016-05-25 | A in MTEP16 |  | West | MPC | Roughrider 230 kV Substation | Add a new Center area 230 kV substation to support a wind farm interconnection. | 2016-12-01 | 2016-12-01 | 5500000 | New wind farm requires a point of interconnection for its site. | 2016-12-01 |  | ND | ND | Planned |  |  |  | 230 | 0 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
11303 | 2016-05-26 | A in MTEP16 |  | West | MPC | Roughrider-Mandan 230 kV Line Uprate | Increase clearance of Roughrider-Mandan line to 200 deg C by fixing all limiting spans. Increase rating to at least 703 MVA (summer emergency) on Roughrider-Mandan. | 2016-12-01 | 2016-12-01 | 765000 | Mitigate interconnection impacts of a generator interconnection. | 2016-12-01 |  | ND | ND | Planned |  |  |  | 230 | 0 | 0 | 16.4 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
11444 | 2016-06-28 | A in MTEP16 |  | West | MPC | Lake Park Substation | Build a new substation that is fed by the Sheyenne-Audubon 230 kV transmission line. Under the initial plan, it will have a transformer (230/69 kV), one 230 kV back-to-back switch, a disconnect on the substation terminus, one 230 kV high-side breaker, and a 69 kV breaker(s) included. Some of the details are subject to change pending a system impact evaluation. | 2017-12-31 | 2017-12-31 | 7000000 | Alternate service to the Hawley, MN, area is required. Also, load service at the Ulrich substation has become constrained. The supporting 115 kV system is beginning to experience voltage support issues, and capacitors would be needed otherwise. | 2017-12-31 |  | MN | MN | Planned |  |  |  | 230 | 0 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Not Applicable | Not Applicable
4813 | 2016-05-25 | A in MTEP16 | B>A | West | MPC, OTP | Clearbrook West 115 kV-Bagley West 230 kV | Clearbrook West to Bagley West 230 kV - new 115 kV transmission line (16 miles) 795 ACSR conductor. Bagley West 230/115 kV new substation. Add 230/115 kV Breakers 140 MVA Transformer & new line termination. Bagley West 230 kV tap. Project taps proposed Clearbrook to Clearbrook West 115 kV radial line. Bagley North 115 kV Switching substation, Add 115 kV 3 Breaker Ring Bus | 2020-12-31 | 2020-12-31 | 12300000 | Support Radial Load & Future Load. Tie two isolated systems together to provide benefits to both NW MN and Winger - Wilton pockets | 2020-12-31 | Clearbrook-Solway 115 kV line. | MN | MN | Planned | BaseRel | Not Shared |  | 230 | 115 | 16 | 0 | 3 | Y | OTP | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
9971 | 2015-09-15 | A in MTEP16 |  | West | OTP | Rugby to Harvey 115 kV Line Rebuild | Starting in 2016, Otter Tail will target a portion of line to rebuild concentrating on the areas where the most concerns have been identified. Otter Tail will continue this strategy until the rebuild is completed, currently estimated to occur during 2021. | 2021-12-31 | 2021-12-31 | 1500000 | Each year, Otter Tail reviews the performance and reliability of transmission lines throughout its system and identifies lines that meet the criteria for improvements. As a result of this process, the existing Harvey – Rugby 115 kV line has been identified as needing improvements due to reliability concerns stemming from the reject rate from ground line inspections, number of breaker operations it experiences and vintage. A multi-year plan has been identified that will rebuild portions of this line each year to mitigate these concerns. The rebuild of this line will involve the replacement of existing structures as well as the re-framing of this line to include Otter Tail’s new vertical design inclusive of a shield wire for lightning protection. | 2021-12-31 |  | ND | ND | Planned | Other |  | Condition | 115 | 0 | 0 | 30 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
9990 | 2015-09-15 | A in MTEP16 |  | West | OTP | Devils Lake East 41.6 kV | Relay upgrades | 2016-12-31 | 2016-12-31 | 37500 | OTP studies has shown additional capacity is needed due to load growth in area. | 2016-12-31 |  | ND | ND | Planned | Other |  | Reliability | 41.6 | 0 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
9995 | 2015-12-30 | A in MTEP16 |  | West | OTP | Devils Lake SW 41.6 kV | Relay upgrades | 2017-12-31 | 2017-12-31 | 37500 | OTP studies has shown additional capacity needed due to load growth in area. | 2017-12-31 |  | ND | ND | Planned | Other |  | Reliability | 41.6 | 0 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
9997 | 2016-06-16 | A in MTEP16 |  | West | OTP | Rolette 230/69/41.6 kV Substation | Tap Xcel's 230 kV line between Rugby and Glenboro and install 230/69/41.6 kV Transformer - Install three 230 kV Breakers, one 69 kV Breaker, one 41.6 kV Breaker and install one 230/69/41.6 kV Transformer (60 MVA). Construct 12 miles of 41.6 kV line and 6 miles of 69 kV line. | 2018-12-01 | 2018-12-01 | 9000000 | Improves reliability by introducing a new high voltage transmission source into the 69 kV and 41.6 kV transmission systems. | 2018-12-01 | Avoid SPP transmission tariff by connecting OTP load to MISO source. | ND | ND | Planned | Other |  | Economic | 230 | 41.6 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
10001 | 2016-06-16 | A in MTEP16 |  | West | OTP | Voltaire 115/41.6 kV Substation | Build a new 115/41.6 kV substation in the Voltaire area by tapping MISO facilities and re-terminating existing OTP - owned 41.6 kV circuits from CPEC - owned Voltaire substation to new OTP - owned 115/41.6 kV delivery. Install one 40 MVA Transformer 115/41.6 kV. Install four 41.6 kV Breakers. | 2018-10-01 | 2018-10-01 | 5000000 | Improves reliability by introducing a new high voltage transmission source into the 41.6 kV transmission system. | 2018-10-01 | Avoid SPP transmission tariff by connecting OTP load to MISO source. | ND | ND | Planned | Other |  | Economic | 115 | 41.6 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
10003 | 2016-06-16 | A in MTEP16 |  | West | OTP | Rugby 230/115/41.6 kV Substation | Install five 41.6 kV Breakers in the Rugby area to re-terminate existing OTP-owned 41.6 kV circuits from CPEC-owned Rugby substation to OTP/MISO 230 kV delivery. | 2018-10-01 | 2018-10-01 | 3000000 | Improves reliability by introducing a new high voltage transmission source into the 41.6 kV transmission system. | 2018-10-01 | Avoid SPP transmission tariff by connecting OTP load to MISO source. | ND | ND | Planned | Other |  | Economic | 230 | 41.6 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
10007 | 2015-09-15 | A in MTEP16 |  | West | OTP | Max to Ryder 41.6 kV Line Upgrade | The project will start in 2016 and be completed in 2018. The project will replace failing insulation, cross arms and poles identified through patrols and inspections and replace the failing 1/0 ACSR conductor for approximately 22 miles between Max, ND and Ryder, ND. | 2018-12-31 | 2018-12-31 | 1228000 | The Max – Parshall 41.6 kV line is a 59 mile radial line serving seven communities in Otter Tail Power Company's service territory. The line has been extensively patrolled and inspected in the last couple of years. On average, the line was installed in the early 1960s. The line has experience numerous weather and electrical events in the fifty plus years of service. Due to the past loading the conductor has experienced, the conductor has fatigued and has mechanically failed numerous times in the past few years. These failures have caused outages and reliability challenges for OTP and its customers. | 2018-12-31 |  | ND | ND | Planned | Other |  | Condition | 41.6 | 0 | 0 | 22 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
10903 | 2016-06-16 | A in MTEP16 |  | West | OTP | Rugby 115 kV Breaker/Line Addition | Rugby 115 kV Breaker/Line Addition - Relocate 230/115 kV Transformer and install a new 115 kV Breaker and 2 miles of line to Rugby-Harvey line. | 2018-10-01 | 2018-10-01 | 1500000 | Improves reliability by introducing a new high voltage transmission source into the 115 kV transmission system. | 2018-10-01 |  | ND | ND | Planned | Other |  | Economic | 230 | 115 | 2 | 0 | 2 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Recommendation
10443 | 2016-02-01 | A in MTEP16 |  | West | RPU | Douglas Trail Substation | New load serving substation (Douglas Trail Substation) will tap RPU's immediately adjacent Q5 161kV transmission line. | 2017-04-01 | 2017-04-01 | 7000000 | Substation is needed to serve Epic's data center load and other RPU loads in the NW part of Rochester | 2017-04-01 |  | MN | MN | Planned | Other |  | Reliability | 161 | 0 | 0.07 | 0 | 1 | Y |  | Rochester Public Utilities | Bottom-Up | Submitted for Recommendation
4696 | 2015-10-22 | A in MTEP16 |  | West | XEL | Rebuild Prentice-Medford 69 kV | Rebuild this line to 795 ACSR due to age and condition of the line | 2018-01-31 | 2018-01-31 | 20145714 | Age and condition rebuild | 2018-12-01 |  | WI | WI | Planned | Other |  | Condition | 69 | 0 | 0 | 33.5 | 1 | Y |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10045 | 2015-09-17 | A in MTEP16 |  | West | XEL | City of Chaska Interconnection | Build an in-and-out from double circuit 115 kV just south of Bluff Creek. This in-and-out will serve the City of Chaska’s new distribution substation. New line will 1.7 mi following road from POI to potential new sub | 2016-06-30 | 2016-06-30 | 3200000 | City of Chaska would like this substation to accommodate future growth, 30+ MW of load. |  |  | MN | MN | Planned | Other |  | Reliability | 115 | 0 | 0 | 0 | 2 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10062 | 2015-09-18 | A in MTEP16 |  | West | XEL | Tyrone Tap Interconnection | Install a 3-way switch on NSP’s St. Thomas Tap to Boright #2 69 kV line. GRE will then construct a radial line from the tap to serve the new MVEC load. | 2016-06-30 | 2016-06-30 | 375000 | GRE requested an interconnection near Sheas Lake to serve between 1 and 5 MW of load. | 2015-12-31 |  | MN | MN | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10063 | 2015-09-18 | A in MTEP16 |  | West | XEL | Rebuild Jackson Co – DPC Merrillan Tap 69 kV | Rebuild 6.1 miles from Jackson Co to DPC Merrillan Tap to 565.3 ACSR/TW. | 2016-07-30 | 2016-07-30 | 3300000 | - Due to sand mine growth at Alma Center, Blair, and DPC Badger Sand, Garden Valley, Cotton School. - Overloads for losses on the of Tremval – Alma Center 69 kV with new loads. - Lower impedance line helps with voltage support to 69 kV system. | 2016-06-01 |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 6.1 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10065 | 2015-09-18 | A in MTEP16 |  | West | XEL | Rogers Lake Overstressed Breaker Replacement | Replace the four existing gas 40 kA breakers at Rogers Lake with with gas 63 kA breakers. | 2016-04-30 | 2016-04-30 | 940847 | - The latest fault current study identified the available fault current at Rogers Lake at 48.44 kA which is excess of the breakers fault current capability (2019) - GRE is requesting to close the N.O. tie with Yankee Doodle to help with load serving issues with Dakota Electric | 2016-06-01 |  | MN | MN | Planned | Other |  | Condition | 115 | 0 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10066 | 2015-09-18 | A in MTEP16 |  | West | XEL | Southtown Area Upgrades | Upgrade the Southtown-Cedarvale 115 kV line to a minimum of 290 MVA emergency. Upgrade the Southtown-Shepard 115 kV line to a minimum of 270 MVA emergency. Add a 80 MVAR cap to the Hiawatha substation. | 2016-06-01 | 2017-12-30 | 3495000 | - The 2014 MNTACT analysis identified these two thermal system deficiencies starting in the year 2015 summer peak for a C3 contingencies - The 2014 MNTACT analysis identified low voltages for the Shepard, Southtown, Hiawatha, and Midtown substation for a C3 contingency starting in 2019 summer peak | 2016-06-01 |  | MN | MN | Planned | BaseRel |  |  | 115 | 0 | 0 | 0 | 3 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10067 | 2015-09-18 | A in MTEP16 |  | West | XEL | MPC Fossum Interconnection | This project will convert the Prairie Substation to a breaker-in-a-half configuration to accommodate MPC’s Fossum 115 kV interconnection request. Fossum will operate radially. | 2018-01-01 | 2018-01-01 | 17261500 | - MPC is requesting interconnection to convert some of their 69 kV load to 115 kV - This interconnection request will be the 12th 115 kV element and the bus needs to be converted to a breaker-in-a half configuration | 2018-01-01 |  | ND | ND | Planned | Other |  | Reliability | 115 | 0 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10068 | 2015-09-18 | A in MTEP16 |  | West | XEL | Install Baytown 2nd Transformer | Install a 2nd transformer and switchgear at Baytown substation. This will require an in-and-out design at Baytown. | 2017-06-01 | 2017-06-01 | 1625468 | This substation is a high consequence risk since if we lose TR1 we cannot pickup 21 MVA out of the 23MVA at the sub. Also, feeders nearby are highly loaded and several N-1’s. | 2016-06-01 |  | MN | MN | Planned | Other |  | Reliability | 115 | 13.8 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10069 | 2015-09-18 | A in MTEP16 |  | West | XEL | Twin Creek Breaker Station | Install a 2 or 3 position 69 kV breaker station - Breakers to Radisson and Osprey/Big Falls - Possible breaker looking toward the Enbridge loads or just switches - Replaces the planned 3-way tap switch on line W3474 that was part of the Enbridge expansion/DPC N-2 retirement plan | 2019-11-01 | 2019-11-01 | 2866000 | Incoming DPC and Enbridge interconnections - Adding 15 MW of new load for Enbridge Removing Trails End breaker as part of Radisson – Osprey project. Now increased exposure for 7 substations: - 50+ miles from Big Falls to Radisson, including Doughty Road, DPC interconnection, and Enbridge radials Puts breaker in middle of loads, can continue to serve Enbridge for fault on lines to Big Falls or Radisson | 2016-11-01 |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10071 | 2015-10-22 | A in MTEP16 |  | West | XEL | Prescott Capacity Upgrade | Install second 69/12.47 kV 28 MVA transformer at Prescott, add additional feeders, and install a second 10 MVAR cap bank. | 2016-09-30 | 2016-09-30 | 1174000 | New Industrial Park Load - Additional 2 MVA - Transformer loaded to capacity - Proposed High School built near Industrial Park N-0 Risks on Prescott | 2016-09-30 |  | WI | WI | Planned | Other |  | Distribution | 69 | 0 | 0 | 0 | 2 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10072 | 2015-09-18 | A in MTEP16 |  | West | XEL | Dean Lake Third Transformer and Ring Bus | Install a 3rd TR at Dean Lake and add 4 new breakers to complete the ring bus. | 2016-08-01 | 2016-12-31 | 4904100 | Interconnection request by City of Shakopee. Third transformer is needed to serve more load and will require a ring bus. | 2016-08-01 |  | WI | MN | Planned | Other |  | Distribution | 115 | 13.8 | 0 | 0 | 2 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10073 | 2015-09-18 | A in MTEP16 |  | West | XEL | GIC Monitoring | This project is to install GIC Monitoring at various substations throughout NSPM/NSPW system. Projects will be modeled after the King GIC monitoring pilot program. Transformers will be selected based upon planning study and geographic location. The first substations to have the GIC monitoring installed will be Quarry, Adams, Elm Creek, and Eau Claire. | 2016-04-30 | 2016-12-31 | 585150 | Assist System Operators in Geomagnetically Induced Current Monitoring to comply with NERC TPL-007-1 and EOP-010-1 standards. | 2016-12-31 |  | WI | MN | Planned | Other |  | Reliability | 345 | 115 | 0 | 0 | 4 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10074 | 2015-09-18 | A in MTEP16 |  | West | XEL | Airport – Rogers Lake 115 kV Rebuild | This project rebuilds the Airport - Rogers Lake 115 kV line due to age and condition. The new line would be built using 795 ACSS conductor. | 2019-05-30 | 2019-05-30 | 4092000 | Age and condition. | 2017-04-01 |  | MN | MN | Planned | Other |  | Condition | 115 | 0 | 0 | 3.4 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10075 | 2015-09-18 | A in MTEP16 |  | West | XEL | Waconia 2nd Distribution Transformer | Install a 2nd distribution transformer at Waconia substation and associated feeders. This new transformer will require the 69 kV yard to be converted to an in-and-out configuration. | 2017-12-30 | 2017-12-30 | 420000 | Local load serving. | 2016-12-01 |  | MN | MN | Planned | Other |  | Reliability | 69 | 13.8 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10076 | 2015-09-18 | A in MTEP16 |  | West | XEL | West St Cloud – Millwood Tap Rebuild | Rebuild 24 miles of line from West St. Cloud to Millwood Tap. This new line will be built using 477 ACSR conductor. | 2019-05-30 | 2019-05-30 | 10400000 | Age and condition. | 2017-12-31 |  | MN | MN | Planned | Other |  | Condition | 69 | 0 | 0 | 24 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10077 | 2015-09-18 | A in MTEP16 |  | West | XEL | GRE St. James Interconnection | Install a new three-way switch with load interrupters to accommodate GRE interconnection on line 0714. | 2016-12-01 | 2016-12-01 | 390800 | GRE interconnection driver. GRE will retire their current St. James substation. | 2016-10-01 |  | MN | MN | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10288 | 2015-10-30 | A in MTEP16 |  | West | XEL | Osprey 69 kV Expansion | Install 69 kV straight bus with 2 additional 69 kV breakers. Reterminate line from Whitetail Tap and Flambeau into Osprey. Rebuild the last 0.4 mies of 69 kV on the Whitetail Tap line to match the rest of the conductor type | 2018-09-01 | 2018-09-01 | 2880000 | Original plan for the Radisson - Osprey 161/69 kV project was to tie the 69 kV rebuild into Big Falls. Upon further evaluation, Big Falls is a old substation, has maintenance concerns, and plan would produce non-standard, hazardous condition for future work. Osprey is a new substation, located next door and better situated to handle the rebuild. Better for the local long term plan in the area | 2018-09-01 |  | WI | WI | Planned | Other |  | Reliability | 69 | 0 | 0 | 0 | 3 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10289 | 2015-10-30 | A in MTEP16 |  | West | XEL | Elmwood - Eau Galle Rebuild | Rebuild the existing 2/0 conductor to 477 ACSR due to age and condition | 2015-12-01 | 2016-12-01 | 2109095 | Age and Condition | 2016-12-01 |  | WI | WI | Planned | Other |  | Condition | 69 | 0 | 0 | 0 | 2 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10290 | 2015-10-30 | A in MTEP16 |  | West | XEL | Gravel Island Distribution | Install a 28 MVA distribution TR and associated breaker and bus work | 2017-08-30 | 2017-08-30 | 2983000 | Xcel Energy's distribution group requested an interconnection at Gravel Island 161 kV | 2015-12-01 |  | WI | WI | Planned | Other |  | Distribution | 161 | 12.5 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
10291 | 2015-10-30 | A in MTEP16 |  | West | XEL | New LCO Hydro Transformer | Install single 34.5/23.9 kV TR to connect the Lac Courte Oreilles (LCO) hydro facility to the NCP system near Radisson | 2018-12-01 | 2018-12-01 | 180000 | North Central Power (NCP) is requilding their existing 23.9 kV system to 34.5 kV in the next 3-4 years. In order to continue connecting the LCO Hydro to the system, a new 34.5/23.9 kV TR is required. | 2018-12-01 |  | WI | WI | Planned | Other |  | Distribution | 34.5 | 23.9 | 0 | 0 | 1 |  |  | Northern States Power (Xcel Energy) | Bottom-Up | Submitted for Recommendation
9719 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Cahokia Bus-Tie 3-4 Upgrade | Upgrade Bus-Tie 3-4 position to 3000 A capability | 2018-06-01 | 2018-06-01 | 0 | 345 kV breaker failure at Cahokia | 2018-06-01 |  | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9723 | 2015-12-14 | B in MTEP16 |  | Central | AmerenIL | Fishhook Breaker Station | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV line. | 2018-12-31 | 2018-12-31 | 0 | Needed to facilitate connection by PPI | 2018-12-31 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9724 | 2016-05-23 | B in MTEP16 |  | Central | AmerenIL | Newton Transformer #1 Retermination. | Relocate Newton 345/138 kV Xfmr #1 345 kV connection point | 2018-06-01 | 2018-06-01 | 0 | Transformer overload following 345 kV breaker failure. | 2018-06-01 |  | IL | IL | Proposed |  |  |  | 345 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9729 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | North Decatur-Clinton Rt.. 54 Upgrade | Reconductor to 1200 A summer emergency capability | 2019-06-01 | 2019-06-01 | 0 | Conductor overload following outage to two 345 kV lines. | 2019-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 5.4 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9734 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | North Utica Substation | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | 2019-06-01 | 2019-06-01 | 0 | Needed to serve local load | 2019-06-01 |  | IL | IL | Proposed |  |  |  | 138 | 34.5 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9738 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Grand Tower-Carbondale Reconductoring | Reconductor to 1200 A summer emergency capability | 2018-06-01 | 2018-06-01 | 0 | Conductor overload following 138 kV breaker failure | 2018-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 16.66 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9739 | 2016-05-17 | B in MTEP16 |  | Central | AmerenIL | Carbondale, Northwest-West Frankfort Reconductoring | Reconductor 3.18 miles conductor in the Carbondale-Reeds section with conductor capable of carrying 1200 A under summer emergency conditions. | 2018-06-01 | 2018-06-01 | 0 | P2-3 HV breaker failure event: Failure of Grand Tower Breaker # 1449 would cause existing conductor to be loaded to 110% of rating in 2020 summer, based on 2015 analysis. | 2018-06-01 |  | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 3.18 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9740 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Grand Tower-Campbell Hill Reconductoring | Reconductor to 1200 A summer emergency capability | 2019-06-01 | 2019-06-01 | 0 | Conductor overload following 138 kV breaker failure. | 2019-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 7.94 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9743 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Pana, North-Route 51D Reconductoring | Reconductor to 2000 A summer emergency capability | 2021-06-01 | 2021-06-01 | 0 | Conductor overload for Generator + Line contingency event. | 2021-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 1.43 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9745 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Ramsey Transformer Replacement | Replace existing transformer with 560 MVA unit | 2018-06-01 | 2018-06-01 | 0 | Transformer overload for outage of two 345 kV lines. | 2018-06-01 | None | IL | IL | Proposed |  |  |  | 345 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9746 | 2015-09-11 | B in MTEP16 |  | Central | AmerenIL | Pana, North-Schram City Reconductoring | Reconductor to 1200 A summer emergency capability | 2018-06-01 | 2018-06-01 | 0 | Conductor overload following outage of two 345 kV lines. | 2018-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 5.19 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9826 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Neoga Transformer Addition | Install 2nd. 345/138 kV, 560 MVA Transformer | 2018-06-01 | 2018-06-01 | 0 | Transformer overload for outage of two 345 kV lines. | 2018-06-01 | None | IL | IL | Proposed |  |  |  | 345 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9832 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Casey-Kansas Reconductoring | Reconductor to 3000 A summer emergency capability | 2027-06-01 | 2027-06-01 | 0 | Conductor loading projected to exceed rating following outage of two EHV lines. | 2027-06-01 | None | IL | IL | Proposed |  |  |  | 345 | 345 | 0 | 21.16 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9838 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Kincaid Terminal Upgrade | Upgrade terminal equipment on Kincaid-Austin 345 kV position. | 2022-06-01 | 2022-06-01 | 0 | Terminal equipment overloading following outage of two 345 kV lines. | 2022-06-01 | None | IL | IL | Proposed |  |  |  | 345 | 345 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9840 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Washington Street Ring Bus | Install 138 kV Ring Bus | 2020-05-01 | 2020-05-01 | 0 | Local load serving need | 2020-05-01 |  | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9841 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | South Bloomington 138-34.5 kV Transformer | Install 112 MVA Transformer | 2019-05-01 | 2019-05-01 | 0 | Local load serving need | 2019-05-01 |  | IL | IL | Proposed |  |  |  | 138 | 34.5 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9842 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Normal East 138-69 kV Transformer | Install 112 MVA Transformer | 2020-05-01 | 2020-05-01 | 0 | Local load serving need | 2020-05-01 |  | IL | IL | Proposed |  |  |  | 138 | 69 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9843 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Normal East 138-34.5 kV Transformer | Install 112 MVA Transformer | 2019-05-01 | 2019-05-01 | 0 | Local load serving need | 2019-05-01 |  | IL | IL | Proposed |  |  |  | 138 | 34.5 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9844 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Normal East-McLean 138 kV Line | Construct 138 kV line | 2020-05-01 | 2020-05-01 | 0 | Local area support | 2020-05-01 |  | IL | IL | Proposed |  |  |  | 138 | 138 | 10 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9846 | 2016-05-23 | B in MTEP16 |  | Central | AmerenIL | Newton Plant 3rd. 345 kV Outlet Line | Construct 345 kV Line from Newton to Casey, West | 2020-12-01 | 2020-12-01 | 0 | Overload to Newton 345/138 kV transformers for outage to two 345 kV lines. |  | Alternatives for line extension under study | IL | IL | Proposed |  |  |  | 345 | 345 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9851 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Edwards-Kewanee-7423 Reconductoring | Reconductor Ameren portion to 1200 A summer emergency capability | 2019-06-01 | 2019-06-01 | 0 | Age and condition of facilities | 2019-06-01 | None | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 1.51 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9857 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Liberty 345/138 kV Substation | Establish 345/138 kV Substation, connect to 138 kV system in Collinsville-O'Fallon-Highland, Illinois area | 2019-06-01 | 2019-06-01 | 0 | Area voltage issues with loss of two 138 kV lines. | 2019-06-01 |  | IL | IL | Proposed |  |  |  | 345 | 138 | 0 | 0 | 4 |  | AMRN51 | Ameren Services Company | Bottom-Up | Submitted for Validation
9867 | 2015-09-14 | B in MTEP16 |  | Central | AmerenIL | Vermilion-N. Champaign Terminal Upgrade | Upgrade terminal equipment | 2018-06-01 | 2018-06-01 | 0 | Age and condition of facilities |  |  | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
10883 | 2016-03-11 | B in MTEP16 |  | Central | AmerenIL | Ina Substation 138 kV Breaker Addition | Install 2000 A, 138 kV PCB on Benton, Northwest-Ina-1 line position. Disconnect old metering on the Ina-Mt. Vernon, South 138 kV line position. | 2018-06-01 | 2018-06-01 | 0 | Increased reliability |  |  | IL | IL | Proposed |  |  |  | 138 | 138 | 0 | 0 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
10885 | 2016-03-11 | B in MTEP16 |  | Central | AmerenIL | Cahokia-Ridge-2 138 kV Terminal Equipment Upgrade | Upgrade terminal equipment at Cahokia and Ridge Substations. | 2018-06-01 | 2018-06-01 | 0 | P6-1-2: Circuit rating would be exceeded for a combination line and transformer outage. | 2018-06-01 |  | IL | IL | Proposed |  |  |  | 138 | 0 | 0 | 0 | 2 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
10886 | 2016-03-11 | B in MTEP16 |  | Central | AmerenIL | South Belleville-Centerville-1586 138 kV Reconductoring | Reconductor approximately 5.6 miles in the 17th Street-Centerville section of south Belleville-Centerville-1586 with conductor capable of carrying 1200 A under summer emergency conditions. | 2019-06-01 | 2019-06-01 | 0 | P6-1-1: Conductor would be overloaded for the concurrent outage of two 345 kV lines. | 2019-06-01 |  | IL | IL | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
3020 | 2015-09-11 | B in MTEP16 |  | Central | AmerenMO | Overton-Columbia Terminal Upgrade | Upgrade terminal equipment at Overton Substation. | 2018-06-01 | 2018-06-01 | 0 | Generator + Line contingency events and breaker overstress. | 2018-06-01 |  | MO | MO | Proposed | BaseRel |  |  | 161 | 161 | 0 | 0 | 4 | Y | AMRN49 | Ameren Services Company | Bottom-Up | Submitted for Validation
9717 | 2016-05-23 | B in MTEP16 |  | Central | AmerenMO | Moberly Terminal Upgrade | Upgrade terminal equipment on Thomas Hill-Moberly-1 161 kV line position. | 2040-06-01 | 2040-06-01 | 0 | Generator + Line contingency event. | 2040-06-01 |  | MO | MO | Proposed |  |  |  | 161 | 161 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9721 | 2015-10-14 | B in MTEP16 |  | Central | AmerenMO | Bland-Tegeler 138 kV Reconductoring | Reconductor line to 1200 A summer emergency capability | 2020-06-01 | 2020-06-01 | 0 | Overload following 345 kV breaker failure. | 2020-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 35 | 2 |  | AMRN46 | Ameren Services Company | Bottom-Up | Submitted for Validation
9728 | 2015-09-11 | B in MTEP16 |  | Central | AmerenMO | Adair Substation Upgrades | Upgrade terminal equipment | 2018-11-15 | 2018-11-15 | 0 | Increase system reliability | 2018-11-15 |  | MO | MO | Proposed |  |  |  | 161 | 161 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9730 | 2016-02-29 | B in MTEP16 |  | Central | AmerenMO | Gray Summit Breaker Replacement | Replace overstressed 138 kV breakers. | 2018-12-01 | 2018-12-01 | 0 | Existing breaker is overstressed. | 2018-12-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9731 | 2016-02-29 | B in MTEP16 |  | Central | AmerenMO | Marshall Breaker Replacment | Replace overstressed Bus-Tie 3-4 138 kV breaker. | 2018-12-01 | 2018-12-01 | 0 | Existing breaker is overstressed. | 2018-12-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9732 | 2016-05-20 | B in MTEP16 |  | Central | AmerenMO | Mason Breaker Replacment | Replace overstressed Bus-Tie 1-2 138 kV breaker. | 2018-12-01 | 2018-12-01 | 0 | Existing breaker is overstressed. | 2018-12-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9733 | 2016-05-23 | B in MTEP16 |  | Central | AmerenMO | Page Breaker Replacment | Replace overstressed 138 kV breakers | 2020-12-01 | 2020-12-01 | 0 | Existing breakers are overstressed. | 2020-12-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 2 |  | AMRN47 | Ameren Services Company | Bottom-Up | Submitted for Validation
9735 | 2016-05-23 | B in MTEP16 |  | Central | AmerenMO | Tyson Breaker Replacement | Replace overstressed 138 kV breakers | 2020-12-01 | 2020-12-01 | 0 | Existing breakers are overstressed. | 2020-12-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 3 |  | AMRN48 | Ameren Services Company | Bottom-Up | Submitted for Validation
9824 | 2016-05-20 | B in MTEP16 |  | Central | AmerenMO | Huster Terminal Upgrade | Upgrade terminal equipment on Sioux-Huster-3 position. | 2018-06-01 | 2018-06-01 | 0 | Terminal equipment would be overloaded for the outage of two 345 kV lines. | 2018-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9825 | 2015-09-14 | B in MTEP16 |  | Central | AmerenMO | Osage Terminal Upgrade | Upgrade terminal equipment on Tegeler-Osage-1 position. | 2021-06-01 | 2021-06-01 | 0 | Equipment overload for the outage of two 345 kV lines. | 2021-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
9828 | 2015-09-14 | B in MTEP16 |  | Central | AmerenMO | Joachim-St. Francois-2 and Boyd Branch-St. Francois-1 - Increase Ground Clearance | Increase ground clearance | 2022-06-01 | 2022-06-01 | 0 | Line exceeds rating for outage of two 345 kV lines. | 2022-06-01 | none | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 25.86 | 2 |  | AMRN50 | Ameren Services Company | Bottom-Up | Submitted for Validation
9830 | 2016-05-23 | B in MTEP16 |  | Central | AmerenMO | Meramec-Joachim-2 Reconductoring | Reconductor to 1600 A summer emergency capability | 2022-06-01 | 2022-06-01 | 0 | Conductor loading projected to exceed rating following outage of two 345 kV lines. | 2022-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 138 | 0 | 15.91 | 1 |  |  | Ameren Services Company | Bottom-Up | Submitted for Validation
10786 | 2016-02-18 | B in MTEP16 |  | Central | IPL | Stout BESS - DPP J401 | New ±20 MVA battery energy storage system at existing Stout substation | 2017-12-31 | 2017-12-31 | 4000 | Automatic Frequency Regulation/Ancillary Services | 2017-12-31 |  | IN | IN | Planned |  |  |  | 138 | 13.8 | 0 | 0 | 2 |  |  | Indianapolis Power & Light Company | Bottom-Up | Submitted for Validation
9943 | 2016-05-18 | B in MTEP16 |  | Central | Vectren | Leonard Road 138/69 kV Transformer Addition and Z94 138 kV Line Loop | Leonard Road 138kV/69kV transformer addition and 138kV line Z94 loop. | 2023-12-31 | 2023-12-31 | 3100000 | Serving customer load and enhanced service reliability. | 2023-12-31 |  | IN | IN | Proposed |  |  |  | 138 | 69 | 0 | 0 | 2 |  | 2016SIGE14 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Validation
9950 | 2016-05-18 | B in MTEP16 |  | Central | Vectren | Y76 69kV Line Rebuild from New Harmony to Northwest | 69kV (Line Y76) rebuild from New Harmony to Northwest> | 2023-12-31 | 2023-12-31 | 10000000 | Aging infrastructure. | 2023-12-31 |  | IN | IN | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 2016SIGE15 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Validation
9953 | 2016-05-18 | B in MTEP16 |  | Central | Vectren | New Toyota South Distribution Substation | 69kV/12kV distribution substation for load growth. | 2020-12-31 | 2020-12-31 | 2500000 | Distribution substation for load growth. | 2020-12-31 |  | IN | IN | Proposed |  |  |  | 138 | 12 | 0 | 0 | 1 |  | 2016SIGE16 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Submitted for Validation
9879 | 2015-09-14 | B in MTEP16 |  | East | CETO | Moore Road-Vrooman 138 kV Line | Construct a new approximately 22 mile 138 kV line between Moore Road and Vrooman Substations, adding 138 kV circuit breakers to each station. | 2019-06-01 | 2019-06-01 | 22000000 | Strengthen the southern Michigan area transmission system to improve voltage and capacity |  |  | MI | MI | Conceptual |  |  |  | 138 | 0 | 22 | 0 | 3 |  |  | Consumers Energy Transmission Owner | Bottom-Up | Submitted for Validation
9909 | 2015-09-15 | B in MTEP16 |  | East | ITCT | 6-Wire Trenton Channel - Jefferson 120 kV Circuits | Six-wiring the Trenton Channel - Jefferson #4 120 kV and Trenton Channel - Horn - Jefferson 120 kV circuits with the existing decommissioned lines on their common structures. This will also require the construction of approximately 0.16 mile of double circuit 954 ACSR to complete the loop in-and-out of Horn station. Additionally, rebuild approximately 0.2 miles of 954 ACSR conductor to 1431 ACSR on the Jefferson-Riverview #2 120 kV circuit. Also install a 120 kV bus-tie breaker at Jefferson and upgrade station equipment at Trenton Channel, Horn, Jefferson, and Riverview | 2018-12-31 | 2018-12-31 | 2400000 | The loss of Navarre 230/120KV transformer plus any section that disconnect one of the two Trenton Channel – Riverview 120 kV paths will cause the branches along the remaining one to become overloaded during peak and off-peak conditions. Also, a breaker fault at Trenton Channel position “KG”, takes out both buses #14 and #17 and disconnects most of the outlets for Trenton Channel generation unit #9. This causes the Trenton Channel – Horn – Jefferson 120 kV circuit to overload during peak and off-peak conditions | 2018-12-31 |  | MI | MI | Proposed |  |  |  | 120 | 0 | 0.16 | 0.2 | 8 |  |  | ITC Transmission | Bottom-Up | Submitted for Validation
4383 | 2016-03-30 | B in MTEP16 |  | East | WPSC | Bradley New Station | This project alleviates an identified thermal violation on the Bradley to Gaines line which is limited by equipment in the Bradley station. In addition, the current configuration of the Bradley and Wayland stations are not desirable from a planning or protection standpoint. The transformer protection clears the entire 138kV bus, there is primarily electromechanical relaying in the Bradley station and there are oil breakers in the Bradley station. This project will upgrade both the Wayland and Bradley busses to ring bus configurations, put the current 138kV and 69kV stations in a common fence, replace oil breakers with SF6 and bring the design up to current Wolverine standards. | 2017-01-01 | 2018-12-31 | 4650000 | Substation contains some of the last remaining oil-filled 138kV breakers and relies on a ground switch for transformer protection. Thermal overload identified on Bradley to Gaines line limited by substation equipment. | 2017-12-31 |  | MI | MI | Proposed | Other | Not Shared | Reconfig | 138 | 69 | 0 | 0 | 4 | Y | Bradley Xmsn | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
8222 | 2016-03-30 | B in MTEP16 |  | East | WPSC | Bradley Station Line Modifications | This project will construct the line modifications required to route lines into the new Bradley station. | 2018-12-31 | 2018-12-31 | 1000000 | Construction to support the upgrade of the Bradley 138kV and 69kV station. |  |  | MI | MI | Proposed | Other |  | Relocation | 138 | 69 | 0 | 0 | 1 |  | Bradley line mods | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
9895 | 2015-11-23 | B in MTEP16 |  | East | WPSC | Graves Crossing to Central Lake Rebuild | Rebuild the Graves Crossing to Central Lake 69kV line, install new poles and hardware with 336ACSR conductor | 2019-12-31 | 2019-12-31 | 3200000 | This 69kV transmission line segment was built in 1975. This line segment has 42% condemned, rotten tops, or damaged structures. Because there are so many poles in need of replacing, it falls within our condition based transmission line rebuild criteria to demolish the existing line and rebuild to our new standard configuration. |  |  | MI | MI | Proposed |  |  |  | 69 | 0 | 0 | 7.9 | 1 |  | GRX-CT | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
9903 | 2015-09-15 | B in MTEP16 |  | East | WPSC | White Cloud to Rogers | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor | 2020-12-31 | 2021-12-31 | 18000000 | This 69kV transmission line segment was built in 1967. This line segment has 78% condemned, rotten tops, or damaged structures. Because there are so many poles in need of replacing, it falls within our condition based transmission line rebuild criteria to demolish the existing line and rebuild to our new standard configuration. |  |  | MI | MI | Proposed |  |  |  | 69 | 0 | 0 | 36 | 3 |  | WC-RG Rebuild | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
9916 | 2015-09-15 | B in MTEP16 |  | East | WPSC | Fairview Station Upgrade | Fairview station upgrade | 2018-12-31 | 2018-12-31 | 900000 | Upgrade the relaying, circuit breakers, bus and switches at the Fairview station. There are 69kV switches at the Fairview station that are limiting the line ratings, the station has both digital and electromechanical relaying which is over 20 years old, and the breakers have started to have seal failures. This project will upgrade the station equipment and install a new control house and protection system. |  |  | MI | MI | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | Fairview Station Upgrade | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
9920 | 2015-09-15 | B in MTEP16 |  | East | WPSC | Graves Crossing Station Upgrade | Upgrade the Graves Crossing station | 2020-12-31 | 2020-12-31 | 500000 | The Graves Crossing station consists of one oil breaker installed in 1977. This project will upgrade to a new circuit breaker and protection and control system. |  |  | MI | MI | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | GRX Station Upgrade | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
10264 | 2015-10-28 | B in MTEP16 |  | East | WPSC | Pellston to Cross Village Rebuild | Rebuild the Pellston to Cross Village 69kV line, install new poles and hardware with 336ACSR conductor | 2020-12-31 | 2020-12-31 | 3600000 | This 69kV transmission line segment was built in 1972. This line segment has 48% condemned, rotten tops, or damaged structures. Because there are so many poles in need of replacing, it falls within our condition based transmission line rebuild criteria to demolish the existing line and rebuild. |  |  | MI | MI | Proposed |  |  |  | 138 | 0 | 0 | 9.08 | 1 |  | Pellston to Cross Village | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
10265 | 2015-10-28 | B in MTEP16 |  | East | WPSC | Gaylord Relay Replacement | Gaylord relay replacement - 138kV Livingston line | 2019-12-31 | 2019-12-31 | 35000 | The Gaylord to Livingston transmission line and stations are protected by relay devices that transmit and receive signals over fiber optic shield wire to trip circuit breakers at the respective stations in case of adverse transmission system conditions. The equipment at Gaylord (Wolverine) and Livingston (ITC/METC) substations has reached the end of its service life and requires replacement. This project shall address costs to replace the equipment at the Wolverine owned station. Project coordination will occur that ITC/METC shall also replace their equipment. |  |  | MI | MI | Planned |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
10266 | 2016-05-18 | B in MTEP16 |  | East | WPSC | East Jordan Station Rebuild | This project will replace the existing equipment at the East Jordan station and upgrade the steel, install new controls, 125v DC battery system and a circuit breaker. | 2019-12-31 | 2019-12-31 | 350000 | The existing East Jordan 69kV oil circuit recloser, battery and control system have reached the end of their designed life expectancy. | 2019-12-31 |  | MI | MI | Planned |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
10267 | 2015-10-28 | B in MTEP16 |  | East | WPSC | Black Lake Station Rebuild | Black Lake Station Rebuild | 2019-12-31 | 2019-12-31 | 350000 | The existing Black Lake 69kV oil circuit recloser, battery and control system have reached the end of their designed life expectancy. This project will replace and upgrade the steel, recloser, controls, and 125v DC battery system. |  |  | MI | MI | Planned |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Submitted for Validation
10203 | 2015-10-12 | B in MTEP16 |  | South | AECC | Shaw to Sardis 115kV | 12.00 mile 115kV line from the AECC Shaw substation to the AECC Sardis substation and tie into a proposed 115kV ring bus at the Sardis substation |  |  | 0 | Help relieve Mabelvale to Woodlawn 115kV line and increase reliability at the Shaw substation by providing a looped feed. | 2020-01-01 |  | AR | AR | Proposed |  |  |  | 115 | 0 | 0 | 0 | 2 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Validation
9716 | 2015-09-11 | B in MTEP16 |  | South | CLECO | Coughlin - Plaisance 138 kV Reconductor | Reconductor Coughlin to Plaisance 138 kV line with 2- 954 ACSS. | 2020-06-01 | 2020-06-01 | 12500000 | Loss of Cocodrie to Ville Platte 230 kV line shows overloads on Coughlin to Plaisance in some of the Future models. Reconductoring this line will relieve the overload condition. |  | At this point we are not sure if we would put 1 conductor or 2. 2 conductors would require rebuilding the line. | LA | LA | Proposed |  |  |  | 138 | 0 | 0 | 17 | 1 |  |  | Cleco Power LLC | Bottom-Up | Submitted for Validation
9718 | 2015-09-11 | B in MTEP16 |  | South | CLECO | Ashmore Rd. - Rork 230 kV line | Tap the existing Hineston to Cocodrie 230 kV line 24 miles from Cocodrie at a new 230 kV substation Ashmore Rd. Build a 64 mile 230 kV line from Ashmore Rd. to Rork substation routed through Oakdale, Kinder and Basile for future load growth. |  |  | 115000000 | Under N-1 Conditions we see overloads on Coughlin to Plaisance 138 kV line for the loss of Cocodrie to Ville Platte 230 kV line under certain dispatch scenarios. Having a second 230 kV line going south from Ashmore Rd. relieves this overload condition. |  |  | LA | LA | Conceptual |  |  |  | 230 | 0 | 64 | 0 | 2 |  |  | Cleco Power LLC | Bottom-Up | Submitted for Validation
7943 | 2015-09-09 | B in MTEP16 |  | South | Entergy-AR | Morrilton E. - Gleason: Rebuild 161kV line | Morrilton E. - Gleason: Rebuild 161kV line | 2026-06-01 | 2026-06-01 | 12728176 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of Keo-White Bluff & Keo-Wrightsville 500kV lines (P2-3, EHV Breaker Failure) causes overload of Morrilton E - Gleason Rebuild 13 miles of 161kV line | 2026-06-01 | Build new 23 mile 500kV line from Mayflower to Holland Bottom | AR | AR | Conceptual | BaseRel |  |  | 161 | 0 | 0 | 13.1 | 1 |  | 15-EAI-005 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9694 | 2016-05-12 | B in MTEP16 |  | South | Entergy-AR | Camden Maguire - Smackover 115kV: Rebuild Line | Re-build 14.32 mile long line to a minimum rating of 882A. | 2024-06-01 | 2024-06-01 | 20706029 | Camden Maguire–Smackover 115 kV line overloads in 2018 and 2019 summer for the loss of McNeil-Stephens 115 kV line. | 2024-06-01 |  | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 14.32 | 1 |  | 16-EAI-003 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9699 | 2015-09-10 | B in MTEP16 |  | South | Entergy-AR | El Dorado Donan 115kV: Add 1-30MVAR Capacitor Bank | Add one 30 MVAR capacitor bank at El Dorado Donan 115 kV substation | 2019-06-01 | 2019-06-01 | 862238 | The El Dorado 115 kV system experiences low voltages when there is a bus fault at the El Dorado EHV 115 kV station | 2019-06-01 |  | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-005 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9700 | 2015-09-10 | B in MTEP16 |  | South | Entergy-AR | Blakely - Mt. Pine South 115kV: Rebuild Line | Re-building the ~2.92 mile long 115 kV line to a minimum line rating of 259 MVA (1300 Amps) | 2020-06-01 | 2020-06-01 | 3972886 | The Blakely Dam-Mountain Pine South 115 kV line overloads when there is a bus fault at Carpenter Dam 115 kV station. | 2020-06-01 |  | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 2.92 | 1 |  | 16-EAI-015 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9701 | 2015-09-10 | B in MTEP16 |  | South | Entergy-AR | Lynch West - NRL Galloway 115kV: Rebuild Line | Upgrade 4.12mi Lynch – NLR Galloway line to a minimum rating of 259 MVA (1300 Amps). Any substation equipment rated below 259 MVA (1300 Amps) needs to be upgraded as well. | 2020-06-01 | 2020-06-01 | 4678800 | The Lynch West-North Little Rock Galloway 115 kV line overloads for a breaker failure at the Keo 500 kV station (loss of Keo-West Memphis 500 kV and Keo-Holland Bottoms 500 kV lines). | 2020-06-01 | Convert Keo 500 kV station to a double-bus/double-breaker configuration | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 4.12 | 1 |  | 16_EAI-010 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9702 | 2015-09-10 | B in MTEP16 |  | South | Entergy-AR | Sylvan Hills - Jacksonville North 115kV: Equipment Upgrade | The line is currently limited to 975 Amps by line bay bus at Sylvan Hills. Upgrading the terminal equipment to a minimum rating of 1200 Amps will eliminate the thermal overloads due to breaker failures. | 2021-06-01 | 2021-06-01 | 25000 | The Sylvan Hills-Jacksonville North 115 kV line overloads for breaker failures at Keo 500 kV station and at Holland Bottoms 500 kV station. | 2021-06-01 |  | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-016 | Entergy Arkansas | Bottom-Up | Submitted for Validation
9710 | 2015-09-10 | B in MTEP16 |  | South | Entergy-AR | Little Rock South 115kV: Reconfigure Station | Reconfigure Little Rock South 115 kV station configuration into a double bus double breaker, breaker and a half, or a ring bus configuration. | 2025-06-01 | 2025-06-01 | 5463000 | The Little Rock South 115 kV station is configured as a single bus single breaker substation. A single bus fault will result in load shed event in the West Little Rock 115 kV network. | 2025-06-01 |  | AR | AR | Conceptual |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EAI-013 | Entergy Arkansas | Bottom-Up | Submitted for Validation
10163 | 2015-10-06 | B in MTEP16 |  | South | Entergy-AR | Jonesboro North: Add second 161kV transformer | Craighead Electric Cooperative Corporation (CECC) is splitting the 13.2 kV bus and adding in a second 161 to 13.2 kV transformer. | 2017-03-01 | 2017-03-01 | 800000 | Normal load growth has increased such that the need for a second transformer is required. | 2017-03-01 |  | AR | AR | Planned |  |  |  | 161 | 13.2 | 0 | 0 | 1 |  |  | Arkansas Electric Coopertive Corporation | Bottom-Up | Submitted for Validation
4611 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Flannery Area Construct new 230-69 kV Substation Also reconfigure 69 kV lines 340 and 749 | Cut the existing 69kV Line 759 Denham Springs to Gloria and the existing 69kV Line 369.3 Gloria to Flannery REA at or near Structure number 92. Also cut the existing 230kV line approximately 7.07 miles from Coly toward Jaguar where it crosses near the same Structure number 92. Construct a new station to bring these lines into a new 230-69kV station. Install a 3 breaker ring bus on the 230kV side and a 5 breaker ring bus on the 69kV side to create a new Flannery area 230-69kV auto-transformer station. The 69kV lines, Gloria to Harelson and Coly to Jones Creek create an intersection. Cut the Harelson to Gloria line 340 at or near structure 73 and cut the Coly to Jones Creek line 749 at or near structure 21. Install a new dead end type structure to reconnect the lines and create Harelson to Jones Creek and Lockhart to Gloria. | 2026-06-01 | 2026-06-01 | 15859000 | Either existing Coly 230-69kV auto #1 or #3 will overload for the (P1) single contingency loss of Coly 230-69kV autos #1, #2, or #3. Additionally the 69 kV Harelson to Line 372A Tap Point will overload during an open breaker contingency (P2-1) at Coly. Likewise the Harelson to Gloria 69 kV line will overload during an open breaker (P2-1) contingency at the Polyform 69 kV substation, and the Lockhart to Coly 69 kV line will overload as well as result in low voltage at Nesser and Jonescreek during an open breaker (P2-1) . | 2026-06-01 | None | LA | LA | Proposed | BaseRel |  |  | 230 | 69 | 0 | 0 | 3 | Y | 16-EGL-024 | Entergy | Bottom-Up | Submitted for Validation
7970 | 2015-09-10 | B in MTEP16 |  | South | Entergy-LA | Minden Area Improvement Ph 2 | Construct new 115 kV substation east of Minden REA and cut-in Minden REA to Arcadia 115 kV line and construct new 115 kV lines to cut the Minden to Sailes 115 kV line in and out of the new substation. | 2026-06-01 | 2026-06-01 | 9592834 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The single contingency loss (P2-1) of Vienna to Trussel Crossing results in low voltages at Trussel Crossing and at the new Reese substation. The same (P2-1) event causes thermal overload on the Minden to Minden REA 115 kV line section. The (P2-1) loss of Minden to Minden REA results in a thermal overload of Vienna - Trussel Crossing. This project mitigates the described (P2-1) issues. The project will also alleviate the thermal loading on Vienna - Trussel Crossing for the contingency loss of Sarepta to Minden 115 kV (P1). " | 2026-06-01 |  | LA | LA | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 3 |  | 15-ELL-002 | Entergy | Bottom-Up | Submitted for Validation
9683 | 2015-09-10 | B in MTEP16 |  | South | Entergy-LA | West Monroe Area 230 kV Reliability Improvement Plan | Install 500/230 kV autotransformer at Perryville 500 kV. Construct double circuit 230 kV and utilize existing 230 kV construct facilities to wind up with Perryville - Selman Field - Rilla 230 kV circuit and Perryville - Dunn 230 kV circuit. Install 230/115 kV autotransformers at Dunn and Rilla. Install 230/69 kV auto at Selman Field. | 2024-06-01 | 2024-06-01 | 80796814 | The P1.3 loss of Sterlington 500 kV AT1 overloads Sterlington AT3. The opposite is also true. A separate 230 kV injection source will help eliminate cascading constraints associated with a failure of the Sterlington substation. | 2024-06-01 |  | LA | LA | Proposed |  |  |  | 500 | 69 | 0 | 0 | 8 |  | 16-ELN-002 | Entergy | Bottom-Up | Submitted for Validation
9687 | 2015-09-10 | B in MTEP16 |  | South | Entergy-LA | Sarepta - Minden 115 kV: Upgrade terminal equipment | Upgrade terminal equipment at Minden 115 kV substation | 2022-06-01 | 2022-06-01 | 553129 | P1.2 loss of Mt Olive - El Dorado 500 kV results in thermal overload of Sarepta - Minden 115 kV circuit. | 2022-06-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELN-006 | Entergy | Bottom-Up | Submitted for Validation
9688 | 2015-09-10 | B in MTEP16 |  | South | Entergy-LA | Dunn - Winnsboro 115 kV: New line | Construct new 230 kV line (energized to 115 kV) from Dunn to Winnsboro. | 2024-06-01 | 2024-06-01 | 67738070 | The P2.1 loss of Baxter Wilson - S Vicksburg results in thermal overload of Swartz - Alto. The P3.2 loss of Grand Gulf and Perryville - Baxter Wilson 500 kV results in overload on Swartz - Alto. Low Hydro conditions at Murray hydro result in higher loadings and overloads on subsequent sections. | 2024-06-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 25 | 0 | 1 |  | 16-ELN-007 | Entergy | Bottom-Up | Submitted for Validation
9689 | 2015-09-10 | B in MTEP16 |  | South | Entergy-LA | Beekman: New distribution substation | Construct a new 115 kV substation on the North Bastrop - Crossett North 115 kV line. | 2020-06-01 | 2020-06-01 | 8990059 | Distribution requires a new substation in Morehouse Parish to serve area load. | 2020-06-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELN-008 | Entergy | Bottom-Up | Submitted for Validation
9764 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Dixie Baker to Baker 69 kV: Reconductor Line | Upgrade the Dixie Baker to Baker 69 kV line section. This includes a reconductor and upgrading substation equipment. | 2026-06-01 | 2026-06-01 | 2963000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Open breaker contingency at Port Hudson 69 kV causes a thermal violation on the Dixie Baker to Baker 69 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2026-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-005 | Entergy | Bottom-Up | Submitted for Validation
9766 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Gloria to Flannery REA 69 kV: Reconductor Line | Upgrade the Gloria to Flannery REA 69 kV line section. | 2019-06-01 | 2019-06-01 | 2071000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Open breaker contingency at Harelson to Line Tap 369 69 kV causes a thermal violation on the Gloria to Flannery 69 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2019-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-007 | Entergy | Bottom-Up | Submitted for Validation
9767 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Harelson to Line 372 Tap 69 kV: Reconductor Line | Reconductor the Harelson to Line 372 Tap 69 kV line. | 2025-06-01 | 2025-06-01 | 5143000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Open breaker contingency at Coly to Lockhart 69 kV causes a thermal violation on the Harelson to Line 372 Tap 69 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2025-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-008 | Entergy | Bottom-Up | Submitted for Validation
9768 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Champagne to Barnett Oil Mill Tap 69 kV: Reconductor Line | Reconductor the Champagne to Barnett Oil Mill Tap 69 kV line. | 2021-06-01 | 2021-06-01 | 8250000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Champagne to Barnett Oil Mill TP 69 kV line sections will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Scott to Carencro 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2021-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-009 | Entergy | Bottom-Up | Submitted for Validation
9769 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Barnett Oil Mill Tap to Sunset 69 kV: Reconductor Line | Reconductor the Barnett Oil Mill Tap to Sunset 69 kV line. | 2024-06-01 | 2024-06-01 | 9926000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Barnett Oil Mill TP to Sunset 69 kV line section will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Scott to Carencro 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2024-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-010 | Entergy | Bottom-Up | Submitted for Validation
9781 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | SWLA69IP Phase 1: Jennings to Lawtag 69 kV L-13 Reconductor | Reconductor the Jennings to Lawtag line. | 2022-06-01 | 2022-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Jennings to Lawtag 69 kV L-13 will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Jennings to Lawtag 69 kV L-14. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2022-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-015 | Entergy | Bottom-Up | Submitted for Validation
9784 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Ford to Lake 69 kV: Reconductor Line | Reconductor the Ford to Lake 69 kV line. | 2025-06-01 | 2025-06-01 | 1552000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Ford to Lake 69 kV line section will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Solac to Contraband 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2025-06-01 |  | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-EGL-018 | Entergy | Bottom-Up | Submitted for Validation
9785 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Scott to Judice 138 kV: Reconductor Line | Reconductor the Scott to Judice 138 kV line. | 2024-12-01 | 2024-12-01 | 11903000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Scott to Judice 138 kV line section will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Meaux to Sellers Rd 230 kV line or the single contingency (P1-3) loss of the Meaux 230-138 kV AT. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor. | 2024-12-01 |  | LA | LA | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-019 | Entergy | Bottom-Up | Submitted for Validation
9789 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Port Hudson 230/69 kV: Upgrade T6 station equipment | Upgrade substation equipment on the T6 autotransformer to upgrade the element. | 2026-06-01 | 2026-06-01 | 100000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Port Hudson 230/69 kV T6 autotransformer overloads in 2026 Summer for the loss of the Horseshoe to Fancy Point 230 kV and Waterford 3. This project will alleviate the thermal overload by upgrading station equipment limiting the autotransformer. | 2026-06-01 |  | LA | LA | Proposed |  |  |  | 230 | 69 | 0 | 0 | 1 |  | 16-EGL-025 | Entergy | Bottom-Up | Submitted for Validation
9793 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Esso to Delmont 230 kV: Reconductor Line | Reconductor the Esso to Delmont 230 kV line. | 2023-06-01 | 2023-06-01 | 2136000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. For the loss of the Willow Glen to Pecue 230 kV line the Esso to Delmont 230 kV line overloads in 2023S. | 2023-06-01 |  | LA | LA | Proposed |  |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-EGL-031 | Entergy | Bottom-Up | Submitted for Validation
9796 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Champagne to Plaisance 138 kV: Reconductor Line & reconfigure to ring bus | Reconductor the Champagne to Plaisance 138 kV line and reconfigure the bus at Champagne into a ring bus. | 2021-12-01 | 2021-12-01 | 11199000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. For the loss of the Ville Platte to Cocodrie 230 kV line the Champagne to Plaisance 138 kV line overloads in 2021W. | 2021-12-01 |  | LA | LA | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-035 | Entergy | Bottom-Up | Submitted for Validation
9797 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Nelson to Lake Charles Bulk 138 kV: Reconductor Line | Reconductor the Nelson to Lake Charles Bulk 138 kV line. | 2023-06-01 | 2023-06-01 | 11416000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Nelson to Lake Charles Bulk 138 kV L-698 coupled with the loss of the Acadia generation (P3-2) causes a thermal overload on the Nelson to Lake Charles Bulk 138 kV L-654. This project will increase the thermal capacity of L-654 by rebuilding the line section between Nelson and Lake Charles Bulk. | 2023-06-01 |  | LA | LA | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-EGL-036 | Entergy | Bottom-Up | Submitted for Validation
9798 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Gypsy to Claytonia 115 kV: Reconductor Line | Reconductor the Gypsy to Claytonia 115 kV line. | 2020-06-01 | 2020-06-01 | 7059000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Snakefarm 230/115 kV Auto and Ninemile unit 5 causes a thermal violation on the Little Gypsy to Claytonia 115 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2023-06-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELL-001 | Entergy | Bottom-Up | Submitted for Validation
9799 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Amite to Holton 115kV: Reconductor Line | Reconductor the Amite to Holton 115 kV line. | 2023-12-01 | 2023-12-01 | 12431000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Bogalusa to Franklinton115 kV line causes a thermal violation on the Amite to Chicken farm to Holton 115 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2023-12-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELL-002 | Entergy | Bottom-Up | Submitted for Validation
9800 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Franklinton 115 kV: Add Cap Bank | Add a capacitor bank to the Franklinton 115 kV substation. | 2020-12-01 | 2020-12-01 | 1156000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Bogalusa to Franklinton115 kV line causes a voltage violation at the Franklinton, Pinecliff, Chicken Farm, and Holton 115 kV stations. This project will alleviate the voltage violations by installing a second 32.4 MVar cap banks at the Franklinton 115 kV station. | 2020-12-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELL-003 | Entergy | Bottom-Up | Submitted for Validation
9802 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Snakefarm to Labarre 230 kV: Reconductor Line | Reconductor the Snakefarm to Labarre 230 kV line. | 2020-06-01 | 2020-06-01 | 3834000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Little Gypsy to Wesco 230 kV and Ninemile unit 5 or 6 causes a thermal violation on the Snakefarm to Labarre 230 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2020-06-01 |  | LA | LA | Proposed |  |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ell-005 | Entergy | Bottom-Up | Submitted for Validation
9803 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Prospect to Goodhope 230 kV: Reconductor Line | Reconductor the Prospect the Goodhope 230 kV line section. | 2020-06-01 | 2020-06-01 | 720000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Waterford to Ninemile 230 kV and Ninemile unit 5 or 6 causes a thermal violation on the Prospect to Good Hope 230 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2020-06-01 |  | LA | LA | Proposed |  |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-ELL-006 | Entergy | Bottom-Up | Submitted for Validation
9804 | 2015-09-13 | B in MTEP16 |  | South | Entergy-LA | Avenue C to Paris Tap 115 kV: Reconductor Line | Reconductor the Avenue C to Paris Tap 115 kV line. | 2022-06-01 | 2022-06-01 | 1153000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Michoud 230/138 kV Auto along with Ninemile Unit 6 causes a thermal violation on the Avenue C to Paris Tap 115 kV line. This project will alleviate the thermal violation by upgrading the line conductor as well as station equipment. | 2020-06-01 |  | LA | LA | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-ELL-008 | Entergy | Bottom-Up | Submitted for Validation
10587 | 2016-05-24 | B in MTEP16 |  | South | Entergy-LA | Churchill 230 kV Project | Construct a new substation named Churchill, south of the Ninemile station with a 5 breaker 230 kV ring bus on the Ninemile to Waterford and the Ninemile to Estell 230 kV lines. Convert the existing Ninemile to Barataria 115 kV line to 230 kV and terminate at Churchill and Barataria. Build new 230 kV station at Barataria and add a new 230/115 kV autotransformer. Convert the Barataria to Alliance 115 kV line to 230 kV operation. Expand the 230 kV Alliance substation to a three breaker ring to accommodate transmission lines to Oakville, Barataria, and the 230-115 kV Autotransformer. | 2026-06-01 | 2026-06-01 | 30659000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The P6-1-1 Loss of Ninemile to Peters Road 230 kV line along with Michoud to Mereaux 230 kV line will overload multiple facilities as the 115 kV system in the area attempts to support the now islanded 230 kV system, primarily thru the Behrman 230-115 kV autotransformer. Low voltage is also on the 230 kV and 115 kV system in the area. | 2026-06-01 |  | LA | LA | Conceptual |  |  |  | 230 | 115 | 0 | 0 | 4 |  | 16-ELL-009 | Entergy | Bottom-Up | Submitted for Validation
10363 | 2016-01-13 | B in MTEP16 |  | South | Entergy-LA | Jaguar to Esso Tap 230kV Line Upgrade | Increase the summer emergency rating by 45 MVA from the current rating. |  |  |  | Economic efficiency | [10 empty] | #N/A | #N/A | #N/A |  |  | Midcontinent Independent System Operator, Inc. | Bottom-Up | Submitted for Validation
7906 | 2015-09-28 | B in MTEP16 |  | South | Entergy-MS | Greenwood to Greenwood SS 115 kV: Upgrade line | Upgrade Greenwood - Greenwood SS 115 kV from 70 MVA to at least 239 MVA. | 2019-12-01 | 2019-12-01 | 10332520 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P3.2 loss of Gerald Andrus SES + loss of McAdams - Indianola 230 kV line overloads Greenwood - Greenwood SS 115 kV " | 2019-12-01 |  | MS | MS | Proposed | BaseRel |  |  | 115 | 0 | 0 | 10.48 | 1 |  | 15-EMI-004 | Entergy | Bottom-Up | Submitted for Validation
7909 | 2015-09-10 | B in MTEP16 |  | South | Entergy-MS | Centreville 115 kV: Install 10.2 MVAR Capacitor bank | Install a 10.2 MVAR capacitor bank at the Centreville 115 kV substation. | 2026-06-01 | 2026-06-01 | 880527 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P2.1 loss of Franklin - Arlington 115 kV, Liberth - Gloster, and Natchez - SE Natchez produces low voltages at Woodville and Centreville 115 kV substations." | 2026-06-01 |  | MS | MS | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 1 |  | 15-EMI-007 | Entergy | Bottom-Up | Submitted for Validation
8520 | 2015-09-10 | B in MTEP16 |  | South | Entergy-MS | Indianola: Install 2nd 230-115 kV autotransformer | Upgrade Andrus 230/115 kV autotransformer. Install 2nd 230/115 kV autotransformer at Indianola. | 2020-06-01 | 2020-06-01 | 9187202 | TPL-001-4 P6 loss of Gerald Andrus 230/115 kV autotransformer plus loss of Indianola 230/115 kV autotransformer results in a cascading load shed event across the Mississippi Delta 115 kV transmission network. P1.2 loss of Gerald Andrus - Indianola 230 kV overloads the Gerald Andrus 230/115. | 2020-06-01 | No suitable alternatives identified | MS | MS | Proposed | BaseRel |  |  | 230 | 115 | 0 | 0 | 2 |  | 15-EMI-009 | Entergy | Bottom-Up | Submitted for Validation
9823 | 2015-09-14 | B in MTEP16 |  | South | Entergy-MS | Franklin 500 kV reconfig | Reconfigure the Franklin 500 kV EHV substation so that the Franklin - Bogalusa and Franklin - McKnight 500 kV lines do not share a common breaker. | 2020-12-01 | 2020-12-01 | 23259564 | The loss of a common shared breaker (P2.3) between the Franklin - Bogalusa and Franklin - McKnight 500 kV lines results in multiple thermal overloads on the south Mississippi 115 kV system. | 2020-12-01 |  | MS | MS | Proposed |  |  |  | 500 | 0 | 0 | 0 | 1 |  | 16-EMI-002 | Entergy | Bottom-Up | Submitted for Validation
9829 | 2015-09-14 | B in MTEP16 |  | South | Entergy-MS | Ray Braswell 500/115 upgrade 115 kV breakers | Upgrade 2-2500A 115 kV breakers on the low side of the Ray Braswell 500/115 kV autotransformer. | 2019-06-01 | 2019-06-01 | 1155335 | The P3.2 loss of the Hinds CCGT with the loss of the Lakeover 500/115 kV autotransformer results in thermal overloading on the Ray Braswell 500/115 kV autotransformer (limited by the 115 kV breakers) | 2019-06-01 |  | MS | MS | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EMI-004 | Entergy | Bottom-Up | Submitted for Validation
9831 | 2015-09-14 | B in MTEP16 |  | South | Entergy-MS | Tillatoba 230 kV Reconfigure | Reconfigure Tillatoba 230 kV from a single bus single breaker to a multiple protection scheme bus (double bus double breaker) | 2019-12-01 | 2019-12-01 | 5808776 | The loss of the Tillatoba 230 kV bus results in low voltages in the Grenada 115 kV area and thermal overloads on the Winona - Sawyer 115 kV line. | 2016-06-01 |  | MS | MS | Proposed |  |  |  | 230 | 0 | 0 | 0 | 1 |  | 16-EMI-006 | Entergy | Bottom-Up | Submitted for Validation
9835 | 2015-09-14 | B in MTEP16 |  | South | Entergy-MS | Horn Lake upgrade 115 kV bus | Upgrade the 115 kV bus at Horn Lake beyond 2000A. | 2026-06-01 | 2026-06-01 | 764924 | The loss of the Getwell 230 kV bus (P2.2) results in thermal overload on the Horn Lake 230/115 kV autotransformer. | 2026-06-01 |  | MS | MS | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | 16-EMI-008 | Entergy | Bottom-Up | Submitted for Validation
9836 | 2015-09-24 | B in MTEP16 |  | South | Entergy-MS | South Jackson - East Jackson 115 kV: Upgrade line | Rebuild South Jackson - East Jackson 115 kV to minimum 1300A. | 2019-06-01 | 2019-06-01 | 2300000 | The loss of Lakeover 115 kV bus results in thermal overload on the South Jackson - East Jackson 115 kV line. | 2019-06-01 |  | MS | MS | Proposed |  |  |  | 115 | 0 | 0 | 1.2 | 1 |  | 16-EMI-009 | Entergy | Bottom-Up | Submitted for Validation
9837 | 2015-09-14 | B in MTEP16 |  | South | Entergy-MS | South Grenada - Elliott 115 kV: Upgrade line | Upgrade South Grenada - Elliott 115 kV line to 260MVA. | 2022-06-01 | 2022-06-01 | 4961042 | The P2.1 loss of Greenwood - Browning 115 kV line causes thermal overloads on the South Grenada - Elliott 115 kV line. This overload will only show up with the Attala 230/115 kV autotransformer out of service (part of project 9827). | 2022-06-01 |  | MS | MS | Proposed |  |  |  | 115 | 0 | 0 | 4.91 | 1 |  | 16-EMI-010 | Entergy | Bottom-Up | Submitted for Validation
9811 | 2015-09-14 | B in MTEP16 |  | South | Entergy-TX | Ponderosa to Fish Creek 138 kV: Reconductor Line | Reconductor the Ponderosa to Fish Creek 138 kV line. | 2026-06-01 | 2026-06-01 | 4247000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of Frontier generation coupled with the loss of the Crockett to Grimes 138 kV line (P3-2) causes thermal overloads on the Ponderosa to Fish Creek 138 kV line. The violation will be mitigated by reconductoring the Ponderosa to Fish Creek 138 kV line. | 2026-06-01 |  | TX | TX | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-ETI-011 | Entergy | Bottom-Up | Submitted for Validation
9820 | 2015-09-14 | B in MTEP16 |  | South | Entergy-TX | Hearne to Calvert 69 kV: Reconductor Line | Reconductor the Hearne to Calvert 69 kV line. | 2020-06-01 | 2020-06-01 | 9500000 | Industrial Customer Connection The addition of customer loads at Calvert and Hearne cause N-0 voltage violations at Calvert 69kV. Reconductor line 85 (16.5 Miles) to 105 MVA rating to mitigate violations. | 2020-06-01 |  | TX | TX | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-ETI-019 | Entergy | Bottom-Up | Submitted for Validation
9821 | 2015-09-14 | B in MTEP16 |  | South | Entergy-TX | Bryan to College Station Area 138 kV: Construct New Line | Build a new 138 kV line from the Bryan substation to a new substation in the College Station Area. | 2024-06-01 | 2024-06-01 | 31500000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The loss of 138kV line College Station to Bryan causes thermal overloads on the 69kV lines from Navasota to Caldwell. To mitigate these violations build a new switching station on 138kV line 490 College Station to Grimes and build a new 138kV, 260MVA line (13 mi) from the new switching station to Bryan. | 2024-06-01 |  | TX | TX | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | 16-ETI-020 | Entergy | Bottom-Up | Submitted for Validation
10964 | 2016-04-06 | B in MTEP16 |  | South | Entergy-TX | Calvert to Hearne 69 kV: Construct New Line | Build a new line from Calvert to Hearne 69kV. | 2018-06-01 | 2018-06-01 | 0 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Under base case scenarios of the load increasing at the Calvert bus will overload the existing 69 kV line. Constructing a new line will alleviate the violations. | 2018-06-01 |  | TX | TX | Conceptual |  |  |  | 69 | 0 | 0 | 0 | 1 |  | 16-ETI-022 | Entergy | Bottom-Up | Submitted for Validation
8202 | 2015-09-18 | B in MTEP16 |  | South | ETEC | Fork Creek - Fred 138kV | Construct new Fred 138 kV substation and new Fred-Fork Creek 138 kV line | 2019-12-31 | 2019-12-31 | 27700000 | Provides transmission point of delivery and offloads distribution system that is at capacity limit. | 2020-08-01 | See SHECO_03_MTEP16, SHECO_05_MTEP16 | TX | TX | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 3 |  | SHECO_04_MTEP16 | East Texas Electric Cooperative Inc. | Bottom-Up | Submitted for Validation
8203 | 2015-09-18 | B in MTEP16 |  | South | ETEC | Fred SW - Fred 138kV | Construct new Fred switching station on Dogwood-Warren 138 kV line, construct new 138kV Fred substation, construct new 138 kV line from Fred switching station to new Fred substation. | 2019-12-31 | 2019-12-31 | 24200000 | Provides transmission point of delivery and offloads distribution system that is at capacity limit. | 2020-08-01 | See SHECO_04_MTEP16, SHECO_05_MTEP16 | TX | TX | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 3 |  | SHECO_03_MTEP16 | East Texas Electric Cooperative Inc. | Bottom-Up | Submitted for Validation
10081 | 2015-09-18 | B in MTEP16 |  | South | ETEC | Fred 138kV Loop Project | Construct new Fred switching station on Dogwood-Warren 138 kV line, construct new 138kV Fred substation, construct new 138 kV line from Fred switching station to new Fred substation, construct new 138kV line from Fred substation to North Buna substation. |  |  | 0 | Transmission solution to provide transmission point of delivery, improve transmission system reliability and offloads distribution system that is at capacity limit. | 2020-08-01 | See SHECO_02_MTEP16 for tying the new Fred substation in between Fork Creek and North Buna substation | TX | TX | Proposed |  |  |  | 138 | 0 | 0 | 0 | 5 |  | SHECO_01_MTEP16 | East Texas Electric Cooperative Inc. | Bottom-Up | Submitted for Validation
10082 | 2015-09-18 | B in MTEP16 |  | South | ETEC | Fred 138kV Loop Project Alt_01 | Construct new 138kV Fred substation, construct new 138kV line from Fred substation to the existing North Buna substation, construct new 138kV line from Fred substation to the existing Fork Creek substation |  |  | 0 | Transmission solution to provide transmission point of delivery, improve transmission system reliability and offloads distribution system that is at capacity limit. | 2020-08-01 | See SHECO_01_MTEP16 for tying the new Fred substation in between Fred switchyard and North Buna substation | TX | TX | Proposed |  |  |  | 138 | 0 | 0 | 0 | 5 |  | SHECO_02_MTEP16 | East Texas Electric Cooperative Inc. | Bottom-Up | Submitted for Validation
10080 | 2016-05-12 | B in MTEP16 |  | South | ETEC, Entergy-TX | Weldon 138kV Tie Line | Construct 138 kV line from existing Mustang Prairie station in AEP-Texas to a new Weldon station to existing Magnolia Groveton station in Entergy-Texas. |  |  | 0 | To address reliability issues caused by new load | 2017-08-01 |  | TX | TX | Proposed |  |  |  | 138 | 0 | 0 | 0 | 5 |  | HCEC_01_MTEP16 | East Texas Electric Cooperative Inc. | Bottom-Up | Submitted for Validation
8443 | 2016-02-01 | B in MTEP16 |  | West | ATC | Replace Rocky Run 345/115 kV T1 Transformer | Replace the thee Rocky Run 345-115 kV transformers with two 500 MVA units. | 2017-12-31 | 2017-12-31 | 22000000 | Reliability | 2017-12-31 |  | WI | WI | Conceptual |  |  |  | 345 | 115 | 0 | 0 | 3 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9928 | 2015-09-15 | B in MTEP16 |  | West | ATC | Re-rate Council Creek - Tomah Industrial Park (Y-121) 69kV Line | Re-rate 1.2 miles of 69 kV line between Council Creek and Tomah Industrial Park. | 2017-11-01 | 2017-11-01 | 0 | Reliability. |  |  | WI | WI | Planned |  |  |  | 69 | 0 | 0 | 1.2 | 1 |  | PR07179 | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9930 | 2016-05-04 | B in MTEP16 |  | West | ATC | Uprate Lost Dauphin - Red Maple 138kV | Lost Dauphin - Red Maple 138-kV line uprate. | 2020-12-01 | 2020-12-01 | 0 | Reliability. |  |  | WI | WI | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 |  | PR07296, 602003, 602026 | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9935 | 2015-09-15 | B in MTEP16 |  | West | ATC | Install Wesmark Substation 2-8 Mvar 69-kV capacitor banks | Wesmark Substation: Install 2-8 Mvar 69-kV capacitor banks. | 2020-06-01 | 2020-06-01 | 0 | Reliability. |  |  | WI | WI | Planned |  |  |  | 69 | 0 | 0 | 0 | 1 |  | PR05844 | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9968 | 2015-09-15 | B in MTEP16 |  | West | ATC | Rebuild 138KV Line X-6 Portage - Staff Substation | Rebuild 138KV Line X-6 Portage - Staff Substation. | 2019-12-31 | 2019-12-31 | 0 | Reliability. |  |  | WI | WI | Planned |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9974 | 2015-09-15 | B in MTEP16 |  | West | ATC | Rebuild 138KV Line X-98 Staff - North Randolph Substation | Rebuild 138KV Line X-98 Staff - North Randolph Substation. | 2019-12-31 | 2019-12-31 | 0 | Reliability. |  |  | WI | WI | Planned |  |  |  | 138 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
9991 | 2015-09-15 | B in MTEP16 |  | West | ATC | Rebuild Racine 345kV Bus | Rebuild Racine 345kV Bus. | 2018-12-31 | 2018-12-31 | 0 | Reliability. |  |  | WI | WI | Planned |  |  |  | 345 | 0 | 0 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
10486 | 2015-12-16 | B in MTEP16 |  | West | ATC | Rebuild Chaffee Creek - Lincoln Pump Station 69 kV | Rebuild line Y-18 Chaffee Creek - Lincoln Pump Station. | 2021-12-31 | 2021-12-31 | 0 | Reliability |  |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 0 | 2 |  | PR06461 | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
10590 | 2016-01-12 | B in MTEP16 |  | West | ATC | Rebuild Academy - Columbus 69kV | Rebuild Academy - Columbus 69kV | 2023-12-31 | 2023-12-31 | 0 | Reliability. |  |  | WI | WI | Conceptual |  |  |  | 69 | 0 | 0 | 2.13 | 2 |  | PR06462 | American Transmission Co. LLC | Bottom-Up | Submitted for Validation
8920 | 2015-12-11 | B in MTEP16 |  | West | GRE | Elisha 115/34.5 | Build 11.4 miles 115 kV from Hubbard to Elisha. Build 4.9 miles 115 kV from Elisha to Potato Lake tap. | 2020-09-01 | 2020-09-01 | 15817000 | Low voltage system intact at Pine Point. Reduce megawatt-mile index. | 2019-05-05 |  | MN | MN | Proposed | Other |  | Distribution | 115 | 34.5 | 17.6 | 0 | 4 | Y |  | Great River Energy | Bottom-Up | Submitted for Validation
10102 | 2016-04-13 | B in MTEP16 |  | West | GRE | Owatonna Area Project | Construct a 33 mile 161 kV line from Freeborn/Hayward to West Owatonna. |  |  |  | During the C3 contingency Faribault Energy Park – West Faribault 115 kV line & Byron – West Owatonna 161 kV line there is low voltage on the system in the Owatonna area. | [10 empty] | #N/A | #N/A | #N/A |  |  | Great River Energy | Bottom-Up | Submitted for Validation
9100 | 2015-05-28 | B in MTEP16 |  | West | ITCM | Burlington Terminal & 4th St-Agency 69kV | Upgrade the Burlington 69kV terminal so the Burlington-South Burlington line is conductor limited. Rebuild the Burlington 4th Street-Agency 69kV line to T2-477 (140MVA). | 2019-12-19 | 2019-12-31 | 0 | Single contingency that will overload the Burlington-South Burlington 69kV and the 4th Street-Agency 69kV lines without restricting generation output in the area. | 2019-12-31 |  | IA | IA | Proposed |  |  |  | 69 | 0 | 0 | 2.51 | 2 |  | Burlington Area 69kV | ITC Midwest | Bottom-Up | Submitted for Validation
9122 | 2015-06-10 | B in MTEP16 |  | West | MDU | East Bismarck-Expressway 115 Upgrade | Replace switches and line jumpers at East Bismarck Jct. on the 115 kV line to Expressway Sub. | 2020-06-01 | 2020-06-01 | 125000 | Loss of Mandan - NW Mandan 115 kV line | 2020-06-01 |  | ND | ND | Planned |  |  |  | 115 | 0 | 0 | 0 | 1 |  |  | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Validation
9140 | 2015-06-12 | B in MTEP16 |  | West | MDU | Coyote-NACO Sub 115 Upgrade | Reconductor Coyote Jct-NACO sub 115 kV line with 477 ACSS | 2020-09-01 | 2020-09-01 | 1270000 | Coyote Jct-NACO sub 115 kV line overloads for loss of Dickinson 230/115 kV transformer | 2020-06-01 |  | ND | ND | Proposed |  |  |  | 115 | 0 | 0 | 7 | 1 |  |  | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Validation
9180 | 2015-06-16 | B in MTEP16 |  | West | MDU | Green River Capacitors | Increase Green River Jct. 15 Mvar capacitors to 20 Mvar | 2020-10-01 | 2020-10-01 | 400000 | Voltage violations on Dickinson, ND area buses for loss of the Dickinson 230/115 transformer | 2020-10-01 |  | ND | ND | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  |  | Montana-Dakota Utilities Company | Bottom-Up | Submitted for Validation
2937 | 2016-06-07 | B in MTEP16 |  | West | MEC | Sub 39: Second 345-161 kV Xfmr | Add a second 345-161 kV xfmr. Expand 345 kV and 161 kV buses. | 2022-06-01 | 2022-06-01 | 10900000 | Needed to mitigate potential thermal overload of 345-161 kV transformation for double contingency. | 2022-06-01 | Continue operating guide or New 345 kV line from Cordova-Sub 91. | IL | IL | Proposed | BaseRel | Shared |  | 345 | 161 | 0 | 0 | 1 | Y | G0103 | MidAmerican Energy Company | Bottom-Up | Submitted for Validation
2938 | 2016-06-07 | B in MTEP16 |  | West | MEC | Uprate Sub 39 - Cordova 345 kV Line | Change out structures to increase rating. | 2021-12-01 | 2021-12-01 | 1300000 | Needed to mitigate potential thermal overload of line for double contingency. | 2021-12-01 | Continue operating guide or New 345 kV line from Cordova-Sub 91. | IL | IL | Planned | BaseRel | Shared |  | 345 | 0 | 0 | 15.5 | 1 | Y | G0104 | MidAmerican Energy Company | Bottom-Up | Submitted for Validation
9642 | 2015-09-08 | B in MTEP16 |  | West | MP | 20 Line Bus Relocation | Move 20 Line (Blackberry - 20L Tap) from Blackberry Bus 2 to Blackberry Bus 1 | 2019-12-31 | 2019-12-31 | 1500000 | Overloads on 62 Line (Blackberry - Nashwauk ckt 1) for Blackberry Bus 2 faults | 2019-12-31 | Capacity upgrade of 62 Line (100C required) | MN | MN | Proposed |  |  |  | 115 | 0 | 0.6 | 0 | 2 |  | 20 Line Bus Relocation | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
9643 | 2015-09-11 | B in MTEP16 |  | West | MP | Little Falls 115 kV Tie Breaker Addition | Add a tie breaker in the Little Falls 115 kV bus. Bus 1 to consist of 163 Line (Little Falls - CWP Little Falls), 46 Line (Little Falls - Mud Lake), and 1TR (115/34 kV). Bus 2 to consist of 868 Line (Little Falls - West St Cloud), 49 Line (Little Falls - Blanchard), 10K Cap Bank, and 2TR (115/34 kV). Line-connected transformer 2TR will need to be reconfigured to connect to Bus 2. | 2017-06-01 | 2017-06-01 | 1000000 | Low voltage at Pepin Lake, Blanchard, Bellevue, and Little Falls for Little Falls bus fault events | 2017-06-01 | Alternatives TBD | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | Little Falls Tie Breaker | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
9644 | 2015-09-11 | B in MTEP16 |  | West | MP | North Shore Cap Banks | Add three cap banks in the North Shore Loop. Establish a shunt cap bank station (2x20 MVAr) on the site of the future North Shore Switching Station near Silver Bay, MN, interconnected to existing Tac Harbor - Silver Bay 115 kV Line. Add a second 138 kV cap bank (1x15 MVAr) at the Hoyt Lakes Substation. | 2017-12-31 | 2017-12-31 | 2500000 | Voltage violations in the North Shore Loop for loss of continuity between Hoyt Lakes & Laskin after idling of Taconite Harbor units & addition of new mining load in the Hoyt Lakes area. | 2017-12-31 | Alternatives TBD | MN | MN | Proposed | BaseRel |  |  | 115 | 0 | 0.1 | 0 | 2 |  | North Shore Cap Banks | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
9646 | 2015-09-08 | B in MTEP16 |  | West | MP | Nashwauk 14 Line Upgrade | Increase capacity of Nashwauk - 14 Line Tap 115 kV line | 2020-05-01 | 2020-05-01 | 500000 | Nashwauk - 14 Line Tap overloads for loss of parallel Nashwauk - National 115 kV Line | 2020-05-01 | Reconductor line | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 4.9 | 1 |  | Nashwauk 14 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
9647 | 2015-09-08 | B in MTEP16 |  | West | MP | 53 Line Upgrade | Increase capacity of existing Nashwauk - National 115 kV Line (53 Line) | 2020-05-01 | 2020-05-01 | 500000 | 53 Line overloads for loss of parallel Nashwauk - National - Hibbing 115 kV Line (14 Line) or Nashwauk - 14 Line Tap segment | 2020-05-01 | None | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 6.2 | 1 |  | 53 Line Upgrade | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
10285 | 2015-10-30 | B in MTEP16 |  | West | MP | Forbes 38-44MW Breaker Failure Relay | Install breaker failure relay on Forbes 38-44MW 115 kV bus tie breaker | 2020-05-01 | 2020-05-01 | 0 | Fault on Forbes Bus 2 followed by failure of the bus tie breaker to operate causes overload on Hibbing - Virginia 115 kV Line. Breaker failure relay will prevent tripping of transmission line remote ends, which will keep post-contingent loading within the line's present emergency rating. | 2020-05-01 |  | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  | Forbes Tie Breaker Failure Relay | Minnesota Power (Allete, Inc.) | Bottom-Up | Submitted for Validation
9655 | 2016-06-28 | B in MTEP16 |  | West | MPC | Thief River Falls Area Substation | Add a new Thief River Falls area load serving substation to support load growth. | 2020-12-31 | 2020-12-31 | 1600000 | Load growth, including a new hospital, in the city of Thief River Falls, is driving the need for a new source to the distribution system. | 2020-12-31 |  | MN | MN | Proposed |  |  |  | 115 | 0 | 1.5 | 0 | 3 |  |  | Minnkota Power Cooperative, Inc. | Bottom-Up | Submitted for Validation
9657 | 2015-09-08 | B in MTEP16 |  | West | MPC | Thief River Falls Capacitor | Second 15 MVAR capacitor bank at Thief River Falls 115 kV. | 2020-12-31 | 2020-12-31 | 500000 | TPL standards have identified post-contingent low votlages in NW MN in the out year models, and automatic UVLS cannot be used after 1/1/21. This is needed for mitigation until Winger-Thief River Falls is in service. | 2020-12-31 |  | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 0 | 1 |  |  | Minnkota Power Cooperative, Inc. | Bottom-Up | Submitted for Validation
10043 | 2015-09-17 | B in MTEP16 |  | West | OTP | Jamestown 345 Breaker Addition | Install an additional 345 kV breaker to meet TPL-001-4 Compliance Standard. | 2020-12-31 | 2020-12-31 | 2000000 | TPL-001-4 Compliance Standard, Category P4 (fault plus stuck breaker) requires two breaker separation between lines on EHV system. | 2020-12-31 | This requirement does not allow interruption of firm service or non-consequential load loss and therefore an additional breaker by creating a ring bus allows the two breaker separation between lines. | ND | ND | Planned |  |  |  | 345 | 0 | 0 | 0 | 1 |  |  | Otter Tail Power Company | Bottom-Up | Submitted for Validation
1850 | 2014-01-31 | B | B | East | ITCT | Hancock 230/120kV Transformer | Cut the Wixom-Quaker 230kV circuit into Hancock Station, install a 230/120kV transformer. | 2020-12-31 | 2020-12-31 | 9000000 | TO System needs: 'Relieves overloads of the Southfield to Sunset 120 kV circuit for the shutdown plus contingency loss of the Quaker - Southfield 120 kV circuit and either the Hancock to Wixom 120 kV circuit or the Drake to Quaker 120 kv circuit Additionally, the Drake-Quaker 120 kV, Quaker-Sunset 120 kV, and the Drexel - Southflied 120 kV circuits are overloaded or heavily loaded in the long term cases.MISO System Needs: Reliability: SP: No overloads on branches are above 95% 85P_5G: Overload on Southfield to Sunset of 96.6% for Planned plus Forced outage of Quaker - Southfield 120kV + _Hancock-Wixom 120kV 85P_1P: No overloads on branches are above 95% 85P_6P: Overload on Southfield to Sunset of 100.5% for Planned plus Forced outage of Quaker - Southfield 120kV + _Hancock-Wixom 120kV 70P_4P: No overloads on branches are above 75% Other System Needs: NA | 2020-12-31 | Alternatives to Reliability needs: Shoulder Peak Case Overloads: Redispatch of total around 1800 MW of generation helps mitigate overload completely | MI | MI | Proposed | BaseRel | Shared |  | 230 | 120 | 0 | 0 | 3 | Y |  | ITC Transmission | Bottom-Up | Validated
1856 | 2014-01-31 | B in MTEP10 | B | East | ITCT | Belle River - Greenwood - Pontiac 345kV cut into Jewell | Cut the Pontiac section of the Belle River-Greenwood-Pontiac 345kV circuit into and out of Jewell station. Utilize an existing unused side of 345kV tower for one of the circuits into Jewell, and relocate the Jewell-Spokane 230kV circuit | 2030-12-31 | 2030-12-31 | 5200000 | The Bloomfield-Hamlin, Bloomfield-Wheeler, Lee-Bunce, Greenwood-Lee, and Northwest Lincoln/Northeast/Northwest 120kV circuits are projected to overload for the maintenance shutdown plus contingency of Belle River ? Lenox plus Belle River- St. Clair 345kV circuits at an 85% load level. Also, the Pontiac 345/120kV transformers #301 and #303 are both projected to overload for the loss of the one plus the Bloomfield-Pontiac 230kV circuit. Lastly, the Pontiac-Joslyn and Pontiac-Giddings 120 kV circuits are projected to overload for maintenance shutdown plus contingency scenarios which involve one of the Pontiac transformers. |  | Alternative 1: Rebuild the conductor on the limiting circuits. This would involve rebuilding 23.9 miles of 120 kV circuit and upgrading terminal equipment at Kilgore. Cost Estimate: $24,850,000 Alternative 2: Build the Goodison Project (P907). Cost Estimate: $50,000,000 | MI | MI | Proposed | BaseRel | Shared |  | 345 | 0 | 0 | 0 | 2 | Y |  | ITC Transmission | Bottom-Up | Validated
2932 | 2015-03-25 | B in MTEP10 | B | East | ITCT | St Antoine-Essex #2 120 kV | Construct 2nd underground cable from St Antoine to Essex (5.1 miles). | 2020-06-01 | 2020-06-01 | 54800000 | The Caniff to Mack, Caniff to Northeast and Essex to St. Antoine 120kV cables are the three feeds into Mack/Essex area. Losing two of the three feeds causes the remaining circuit to overload in the off peak models (with Connors creek offline) | 2020-06-01 | Alternative 1:Construct approximately 8.5 miles of 120 kV XLPE cable from Waterman to Essex. Cost Estimate: $85,200,000 Alternative 2:Install approximately 8.5 miles of 230 kV 1500CU XLP cable from Waterman to Essex and put a new 230/120 kV transformer at Essex. Cost Estimate: $92,000,000 | MI | MI | Proposed | BaseRel | Shared |  | 120 | 0 | 5.1 | 0 | 1 | Y |  | ITC Transmission | Bottom-Up | Validated
3210 | 2014-01-31 | B in MTEP10 | B | East | METC | Vanderbilt - Riggsville 138 kV Rebuild | Rebuild 30.3 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. | 2016-06-01 | 2016-06-01 | 33254000 | The Vanderbilt to Riggsville 138 kV circuit is projected to overload for various contingencies for projected peak and off peak system loadings. The contingencies include a single transmission outage, a single transmission line plus a generator, as well as various shutdown plus contingency scenarios at reduced system loading. Most contingencies involved the Emmet to Livingston 138 kV circuit. | 2016-06-01 | Alternaitve 1: Rebuild approximately 30.3 miles of the Livingston to Riggsville 138 kV circuit to 954 ACSR future double circuit 138kV structures. Cost Estimate: $33,254,000 Alternative 2: Rebuild the Livingston to Emmet and Emmet to Oden 138kV circuits with 954 ACSR DCT, creating two circuits from both Livingston to Emmet and Emmet to Oden. Cost Estimate: $38,700,000 Alternative 3: Construct a 30 mile circuit from Stover to Emmet 138kV with 954 ACSR DCT. Cost Estimate: $46,200,000 | MI | MI | Proposed |  |  |  | 138 | 0 | 0 | 30.3 | 1 | Y |  | METC | Bottom-Up | Validated
1746 | 2011-12-13 | B in MTEP10 | B | West | ITCM | Lakefield-Adams 161 kV Rebuild | Rebuild Lakefield-Fox Lake-Rutland-Winnebago-Hayward-Adams 161 kV line to double circuit 345 & 161 kV. Allow for a 345 kV line position for future use. | 2014-12-31 | 2018-12-31 | 97580000 | Rebuild Lakefield-Fox Lake-Rutland-Winnebago-Hayward-Adams 161 kV line to double circuit 345 & 161 kV. Allow for a 345 kV line position for future use. |  |  | MN | MN | Proposed | BaseRel |  |  | 161 | 0 | 0 | 139.38 | 5 | Y |  | ITC Midwest | Bottom-Up | Validated
2935 | 2012-06-21 | B in MTEP10 | B | West | MPW | Reconductor 69 kV lines South - Wiggins - Power Plant (Lines 81 & 82) | MPW is looking at upgrading the 69 kV transmission lines from 633501 South Sub to 633511 Wiggins Road (Line 82) and from 633511 Wiggins Road to our 633408 Power Plant (Line 81) from 58 MW to at least 89 MW (636 ACSR). | 2020-06-01 | 2020-06-01 | 300000 | 1. Overload of lines for contingencies involved in the loss of the existing 134 MVA 161/69 kV transformers at Unit 9. 2. 2012 Summer load of 141.5. 3. Existing 69 kV Lines 82 between South - Wiggins overloaded. 4. Age of lines. | 2020-06-01 | MPW could upgrade only 69 kV transmission lines from 633501 South Sub to 633511 Wiggins Road (Line 82) from 58 MW to at least 89 MW (636 ACSR). Could also reconductor using 477 ACSS. | IA | IA | Proposed | Other | Not Shared | Reliability | 69 | 0 | 0 | 5 | 2 | Y | MPW-WR | Muscatine Power & Water (Board Of Water, Electric & Communications) | Bottom-Up | Validated
2973 | 2014-11-17 | B in MTEP11 | B | Central | AmerenMO | Howard Bend Substation Connection | Howard Bend 138-12 kV Substation - Provide 138 kV ring bus connection from Mason-Carrollton-8 138 kV line to new Howard Bend Substation. Install 1-138 kV, 2000 A PCB at Carrollton Substation as a bus-tie. | 2022-12-01 | 2022-12-01 | 1371000 | New substation connection to serve new load | 2022-12-01 |  | MO | MO | Proposed | Other | Not Shared | Distribution | 138 | 0 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
1815 | 2014-01-31 | B in MTEP11 | B | East | METC | Chase - Mecosta 138kV Rebuild | Rebuild 7.2 miles of 138kV 110 and 115 CU to 954 ACSR. Prebuild to 230kV construction. | 2020-06-01 | 2020-06-01 | 8900000 | Shutdown plus contingency overload involving Cobb-Felch and either Croton-Piston Ring 138 kV or Four Mile-Piston Ring 138 kV Lines | 2020-06-01 |  | MI | MI | Planned | BaseRel | Shared |  | 138 | 0 | 0 | 7.2 | 1 | Y |  | METC | Bottom-Up | Validated
3215 | 2013-09-15 | B in MTEP11 | B | West | MEC | Sub 49 161 kV Capacitor | Add 50 MVAr 161 kV capacitor | 2018-06-01 | 2018-06-01 | 840000 | Required to mitigate double contingency voltage reliability violation on 161 kV facilities. | 2018-06-01 |  | IL | IL | Proposed | BaseRel | Not Shared |  | 161 | 0 | 0 | 0 | 1 | Y | T6242 | MidAmerican Energy Company | Bottom-Up | Validated
3266 | 2013-09-15 | B in MTEP11 | B | West | MEC | Sub 56-89 161 Line Uprate | Increase 161 kV line rating. | 2024-06-01 | 2024-06-01 | 680000 | Required to mitigate double contingency overload of 161 kV line | 2024-06-01 |  | IA | IA | Proposed | BaseRel | TBD |  | 161 | 0 | 0 | 22 | 1 | Y | T6164 | MidAmerican Energy Company | Bottom-Up | Validated
2290 | 2015-09-11 | B in MTEP12 | B | Central | AmerenIL | Joppa 345 kV Switching Station 2nd. Xfmr | Add 2nd. 345/161 kV, 560 MVA Transformer | 2023-06-01 | 2023-06-01 | 0 | For an outage to the Shawnee 500/161 kV transformer, with Prairie State Units 1 or 2 offline, the existing transformer would be loaded to 105% in 2025 summer. |  |  | IL | IL | Proposed | Other | Not Shared | Reliability | 345 | 161 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
2295 | 2015-09-14 | B in MTEP12 | B | Central | AmerenIL | W. Mt. Vernon-E. W. Frankfort 345 kV | Upgrade terminal equipment to 3000 A summer emergency capability at West Frankfort | 2018-06-01 | 2018-06-01 | 0 | Age and condition of existing facilities |  | None | IL | IL | Proposed | Other |  |  | 345 | 0 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3336 | 2012-03-06 | B in MTEP12 | B | Central | AmerenIL | Gilman-Watseka Reconductoring | Reconductor to 1600 A summer emergency capability | 2020-06-01 | 2020-06-01 | 4763000 | For outage of Goodland-Morrison Ditch 138 kV, Gilman-Watseka would be loaded to 103% of rating in 2011 Fall. | 2014-06-01 |  | IL | IL | Proposed | BaseRel |  |  | 138 | 0 | 0 | 15.21 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3342 | 2014-11-17 | B in MTEP12 | B | Central | AmerenIL | Diamond Star-McClean County Sw. Station - Increase Ground Clearance | Increase ground clearance on 2.4 miles of 477 kcmil ACSR conductor | 2025-06-01 | 2025-06-01 | 240000 | For the outage of the Brokaw-Pontiac 345 kV line, with Hennepin Unit #2 offline, this line section would be loaded to 102% of rating in 2015 summer. | 2025-06-01 |  | IL | IL | Proposed | BaseRel |  |  | 138 | 0 | 0 | 5.04 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3687 | 2015-06-09 | B in MTEP12 | B | Central | AmerenIL | North Decatur 138-34 kV Substation - Replace 138 kV Breakers | North Decatur 138-34 kV Substation - Replace 138 kV circuit breaker 1313 in the North Decatur-Clinton Route 54 line with a minimum 2000 A continuous 40 kA interrupting circuit breaker. Upgrade other limiting terminal equipment to a minimum of 2000 A. | 2017-06-01 | 2017-06-01 | 500000 | 5000 MVA circuit breaker at 100% of its interrupting capability. | 2019-06-01 | None | IL | IL | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3703 | 2015-09-11 | B in MTEP12 | B | Central | AmerenIL | New Berlin 138-69 kV Sub | New Berlin 138-69 kV Substation - Install new 112 MVA, 138-69 kV Substation. Connect to Auburn, North-Jacksonville Industrial 138 kV Line 1306. | 2020-06-01 | 2020-06-01 | 0 | Local distribution load | 2020-06-01 | None | IL | IL | Proposed | Other |  | Distribution | 138 | 69 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3701 | 2012-03-06 | B in MTEP12 | B | Central | AmerenMO | Cotter Creek 138-34.5 kV Substation Supplies | Cotter Creek 138-34.5 kV Substation - Provide 138 kV supplies to new Cotter Creek Substation. This will consist of installing a 2000 A, 138 kV PCB at Joachim Substation, and extending new 138 kV line from Joachim to Cotter Creek Substation. Also, for the second 138 kV supply to Cotter Creek, a new 3-2000 A breaker 138 kV switching station (Olympian Village) will be established in the Joachim-St. Francois-2 138 kV line, with a 138 kV line extended from Olympian Village Switching Station to Cotter Creek Substation. | 2023-06-01 | 2023-06-01 | 31230640 | Increase capacity to serve local distribution load | 2017-06-01 | None | MO | MO | Proposed | Other |  | Distribution | 138 | 0 | 0 | 0 | 3 | Y | AMRN25 | Ameren Services Company | Bottom-Up | Validated
3708 | 2012-03-06 | B in MTEP12 | B | Central | AmerenMO | Fountain Lake 2nd. Transformer | Install 2nd. 138-12.5 kV Transformer | 2018-06-01 | 2018-06-01 | 0 | Local distribution load serving needs | 2018-06-01 | None | MO | MO | Proposed | Other |  | Distribution | 138 | 12.5 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
1295 | 2014-01-31 | B in MTEP12 | B | East | ITCT | Quaker to Southfield #2 120 kV | Rebuild the existing Quaker to Drexel to Southfield circuit utilizing 1431 ACSR conductor on double circuit 230 kV towers and add a second Quaker to Southfield circuit on this new tower line | 2018-06-01 | 2018-06-01 | 51050000 | Various combinations of shutdown plus contingency scenarios involving the circuits in or feeding the Southfield area have been shown to cause overloads on the circuits remaining in service. | 2018-06-01 | Cut the Quaker - Wixom 230 kV circuit into Hancock substation and install a 230/120 kV step-down transformer. This alternative will strengthen the Hancock - Southfield 120 kV line to support the area under contingencies. However, this does not relieve the majority of the potential overloads and actually creates several new potential overloads. | MI | MI | Proposed | BaseRel | Shared |  | 120 | 0 | 7.35 | 7.35 | 2 | Y |  | ITC Transmission | Bottom-Up | Validated
2933 | 2014-01-31 | B in MTEP12 | B | East | ITCT | Superior - Wayne 120 kV Reconductor | Re-conductor approximately 10.5 miles of 477 ACSR conductor of the Superior ? Wayne 120 kV circuit to 795 ACSR. | 2016-06-01 | 2016-06-01 | 6000000 | Approximately 10.5 miles of the Superior ? Wayne 120 kV circuit comprised of 477 ACSR conductor is projected to be overloaded for the shutdown plus contingency scenario involving the Superior ? Wayne ? Zebra 120 kV circuit and the Coventry 345-138 kV tran | 2016-06-01 |  | MI | MI | Proposed | BaseRel | Not Shared |  | 120 | 0 | 0 | 10.5 | 1 | Y |  | ITC Transmission | Bottom-Up | Validated
3589 | 2014-01-31 | B in MTEP12 | B | East | ITCT | Lee - Menlo 120 kV Rebuild | Rebuild approximately 5.4 miles of 267 ACSR conductor to 954 ACSR between Lee and the Lake Huron Pumping Tap and approximately 6.4 miles of 267 ACSR conductor to 954 ACSR between Menlo and the Lake Huron Pumping Tap and replace station equipment Lee and M | 2018-06-01 | 2018-06-01 | 11200000 | The Lee to Lake Huron Pumping Tap section of the Lee to Menlo circuit was shown to overload in both the 50/50 and 70/30 peak load models for the N-1-1 scenario involving the Belle River to St. Clair and Belle River to Lenox 345 kV circuits. The Menlo to L | 2018-06-01 |  | MI | MI | Proposed | BaseRel | Shared |  | 120 | 0 | 0 | 11.8 | 2 | Y |  | ITC Transmission | Bottom-Up | Validated
3137 | 2014-01-31 | B in MTEP12 | B | East | METC | Warren - Bard Road 138 kV Rebuild | Rebuild approximately 19.6 miles of the Warren to Bard Road 138 kV circuit to 230 kV double circuit construction using 954 ACSR. One side would be energized at 138kV, with the other side left vacant for future use. Also replace terminal equipment at Bard Road. | 2017-12-31 | 2017-12-31 | 27800000 | The Warren to Bard Road 138 kV circuit is projected to overload for a shutdown plus contingency scenario for projected off-peak system loads for the loss of the Tittabawassee to Gallagher to Livingston 345 kV circuit plus the Ausable (Saginaw River to Twining) 138 kV circuit. | 2017-12-31 |  | MI | MI | Planned | BaseRel | Shared |  | 138 | 0 | 0 | 19.6 | 1 | Y |  | METC | Bottom-Up | Validated
3582 | 2014-01-31 | B in MTEP12 | B | East | METC | Bullock - Summerton 138 kV Rebuild | Rebuild the entire circuit between Bullock and Summerton to 954 ACSR on single-circuit, 138 kV steel pole structures and replace the terminal equipment at Bullock | 2017-06-01 | 2017-06-01 | 20000000 | The Bullock to Summerton 138 kV circuit is projected to be overloaded for various single contingencies at peak and shoulder-peak load and various shut down plus contingency scenarios at projected shoulder-peak load in 2016. Most contingencies involve the Begole to Redstone 138 kV circuit. | 2017-06-01 |  | MI | MI | Proposed | BaseRel | Shared |  | 138 | 0 | 0 | 25.5 | 1 | Y |  | METC | Bottom-Up | Validated
3594 | 2014-11-04 | B in MTEP12 | B | East | METC | Tittabawassee 345 kV Station Equipment Upgrades | Replace 345kV station equipment in rows 34 and 36 at Tittabawassee. | 2018-12-31 | 2018-12-31 | 3500000 | The positions of station equipment in row 34 at Tittabawassee 345kV are projected to become overloaded for the following system conditions: -Position 34F7 when the breaker at Position 34R8 is open and the MCV ? Tittabawassee 1 345 kV circuit is outaged. -Position 34H9 when the breaker at Position 34R8 is open and the MCV ? Tittabawassee 1 345 kV circuit is outaged. -Position 34R8 when the breaker at Position 34F7 is open and the MCV ? Tittabawassee 1 345 kV circuit is outaged. The positions of station equipment in row 36 at Tittabawassee 345kV station equipment are projected to become nearly overloaded for the following system conditions: -Position 36F7 when either the breaker at Position 36H9 or Position 36R8 is open and the MCV ? Tittabawassee 2 345 kV circuit is outaged. -Position 36H9 when the breaker at Position 36F7 is open and the MCV ? Tittabawassee 2 345 kV circuit is outaged. -Position 36R8 when the breaker at Position 36F7 is open and the MCV ? Tittabawassee 2 345 kV circuit is outaged. | 2018-12-31 | Re-terminating circuits into Tittabawassee to alter station flows was considered; however, no viable option exists without crossing several lines and affecting reliability. | MI | MI | Proposed | BaseRel | Not Shared |  | 345 | 0 | 0 | 0 | 1 | Y |  | METC | Bottom-Up | Validated
3659 | 2016-06-28 | B in MTEP12 | B | West | OTP | Roberts County 115/69/41.6 kV Substation | New 115/69/41.6 kV Substation ( joint with WAPA and East River Electric Cooperative ) | 2018-11-01 | 2018-11-01 | 2000000 | Load Serving issues in the Browns Valley area with the existing 41.6 kV system during winter peak conditions | 2018-11-01 | Increase rating of Browns Valley 230/41.6 kV transformer | SD | SD | Proposed | Other | Not Shared | Reliability | 115 | 41.6 | 0 | 0 | 1 | Y | OTP | Otter Tail Power Company | Bottom-Up | Validated
3661 | 2016-06-28 | B in MTEP12 | B | West | OTP | Grenville 69/41.6 kV Substation | Build a new 69/41.6 kV Substation between Otter Tail Power and East River Electric Systems | 2017-12-31 | 2017-12-31 | 700000 | Load Serving issues in the Browns Valley area with the existing 41.6 kV system during winter peak conditions | 2019-12-31 |  | SD | SD | Proposed | Other | Not Shared | Reliability | 69 | 41.6 | 2 | 0 | 2 | Y | OTP | Otter Tail Power Company | Bottom-Up | Validated
3664 | 2016-06-28 | B in MTEP12 | B | West | OTP | Mooreton - Roberts Jct (Abercrombie) 41.6 kV Line | Build 16 miles of new 41.6 kV line | 2018-12-31 | 2018-12-31 | 3800000 | Outage of Wahpeton source creates voltage and loading concerns on the 41.6 kV system | 2018-12-31 | Capacitor banks on the 41.6 kV system | ND | ND | Proposed | Other | Not Shared | Reliability | 41.6 | 0 | 16 | 0 | 1 | Y | OTP | Otter Tail Power Company | Bottom-Up | Validated
4069 | 2012-09-15 | B in MTEP13 | B | Central | AmerenIL | Stalllints Substation Bus-Tie Breaker Addition | Install 2-138 kV, 2000 A bus-tie breakers | 2016-06-01 | 2016-06-01 | 897220 | C2: Failure of the exisiing 138 kV Bus-Tie Breaker would cause voltage violations. Voltages near Stallings would be approximately 90% of nominal or less during 2016 summer, based on 2011 analysis. Installing additional bus-tie breakers would provide support to Stallings should breaker failure occur. | 2016-06-01 | None | IL | IL | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
4071 | 2014-11-17 | B in MTEP13 | B | Central | AmerenIL | Wood River-Stallings 138 kV Line Upgrade | Wood River-Stallings 138 kV Line 1456 - Increase clearances to ground on 5.63 miles of 477 kcmil ACSR between Cottage Hills and Wanda to permit operation at 120 degrees C. Reconductor 6.01 miles of 477 kcmil ACSR in the Stallings-Wanda section with conductor capable of carrying 1600 A under summer emergency conditions. Replace or reconnect 600 A CTs and replace an 800 A PCB at Cottage Hills with equipment capable of carrying 1200 A continuously. | 2025-06-01 | 2025-06-01 | 11004000 | C1: Existing conductor would be loaded to 114.5% of its rating for an outage to the Wood River south 138 kV bus, based on 2011 analysis. | 2025-06-01 | None | IL | IL | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 11.64 | 3 | Y | AMRN31 | Ameren Services Company | Bottom-Up | Validated
4067 | 2015-09-11 | B in MTEP13 | B | Central | AmerenMO | Meramec-Watson-2 138 kV Line Reconductoring | Reconductor 3.7 miles to 1600 A summer emergency capability. | 2018-06-01 | 2018-06-01 | 2107484 | For an outage to the Baumgartner-Watson-1 and Central-Watson-1 138 kV lines, the existing conductor would be loaded to 117% of rating in 2020 summer. | 2018-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 0 | 0 | 3.7 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
4075 | 2014-11-17 | B in MTEP13 | B | Central | AmerenMO | Sioux-Huster-3 138 kV Reconductoring | Reconductor 5.9 miles of 954 kcmil ACSR with conductor capable of carrying 1600 A under summer emergency conditions. Replace 1200 A terminal equpment (dixconnect switches, CT's, bus conductor) at Huster with equipment capable of carrying 1600 A or better. | 2024-06-01 | 2024-06-01 | 5900000 | Line and Generator: Existing conductor would be loaded to about 104% of its rating for an outage to the Sioux-Belleau-6 345 kV Line with Callaway generation offline in 2021 summer, with 1-in-10 load levels, based on 2011 analysis. | 2024-06-01 | None | MO | MO | Proposed |  |  |  | 138 | 0 | 0 | 5.9 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
4346 | 2015-11-13 | B in MTEP13 | B | East |  | Karn-Garfield 138kV Rebuild | Rebuild the 33.5 mile copper portion of the Karn to Garfield circuit using single circuit 138kV structures and 954 ACSR conductor. Mitigate several additional points of interest on the remaining portions (795 and 1431 ACSR). Replace station equipment at |  |  |  | Extensive Sag limits throughout circuit. N-1-1 loss of Karn-Saginaw River 138kV plus Atlanta-Karn-Thetford 138kV. The Karn-Garfield 138 kV circuit also showed up as a constraint in the Long Term Generator Deliverability study conducted by MISO. | 2018-12-31 | Remediate Sag limits to minimum operating rating only (maintain circuit rating of 134 MVA). A different alternative is to address sag clearance issues on the Karn - Garfield 138 kV circuit to increase the rating up to 160 MVA by removing the 3 lower condu | MI | MI |  |  |  |  | 138 | 0 | 0 | 33.5 | 1 |  |  | METC | Bottom-Up | Validated
4012 | 2016-06-30 | B in MTEP13 | B | West | GRE | Hardy Lake Substation (CWP) 115 kV | GRE will build new Crow Wing Power 115 KV Hardy Lake Substation | 2020-12-31 | 2020-12-31 | 207500 | New distribution load | 2020-12-31 | None | MN | MN | Proposed | Other | Not Shared | Distribution | 115 | 0 | 0.1 | 0 | 1 | Y | 20326 | Great River Energy | Bottom-Up | Validated
4013 | 2012-09-11 | B in MTEP13 | B | West | GRE | Air Lake (DEA) 115 kV Substation | GRE will build new Dakota Electric 115 kv South Air Lake substation. | 2026-05-02 | 2026-05-02 | 864000 | New distribution load | 2016-05-01 | None | MN | MN | Proposed | Other | Not Shared | Distribution | 115 | 0 | 0 | 0 | 1 | Y | 20334 | Great River Energy | Bottom-Up | Validated
4015 | 2014-12-19 | B in MTEP13 | B | West | GRE | Le Homme Dieu 115 kV | GRE will convert Runestone's LeHommeDieu 69 kV distribution sub to 115 kV | 2027-12-31 | 2027-12-31 | 365000 | Load is creating 41.6 kV service issues. Move to nearby 115 kV system | 2027-12-31 | Rebuild 41.6 kV facilities | MN | MN | Proposed | Other | Not Shared | Distribution | 115 | 0 | 0 | 0.5 | 1 | Y | 20414 | Great River Energy | Bottom-Up | Validated
4016 | 2016-06-30 | B in MTEP13 | B | West | GRE | Cashel 115 kV conversion | GRE will convert Agralite Cashel 41.6 kV distribution sub to 115 kV | 2022-05-31 | 2022-05-31 | 625000 | Load is creating 41.6 kV service issues. Move to nearby 115 kV system | 2022-05-31 | Rebuild 41.6 kV facilities | MN | MN | Proposed | Other | Not Shared | Distribution | 115 | 0 | 0 | 1 | 1 | Y | 20507 | Great River Energy | Bottom-Up | Validated
3756 | 2015-05-07 | B in MTEP13 | B | West | MP | Wrenshall | Add Transformer and breakers at Wrenshall | 2020-12-31 | 2020-12-31 | 3000000 | reliability |  | Rebuild existing 46 kV circuit | MN | MN | Proposed | TBD |  |  | 115 | 69 | 0 | 0 | 1 | Y | Wrenshall | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
4295 | 2015-06-10 | B in MTEP13 | B | West | MP | HVDC Valve Hall Replacement | Modernization of HVDC terminals at Arrowhead & Square Butte | 2020-12-31 | 2020-12-31 | 75000000 | Modernization/Age & Condition | 2017-12-31 | Project 3856: "HVDC 750MW Upgrade" includes valve replacement in addition to other upgrades necessary for increase to 750 MW capacity | ND | MN | Proposed | Other | Not Shared | Condition | 250 | 0 | 0 | 0 | 2 | Y | HVDC Valve Hall Replacement | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
4482 | 2014-12-17 | B in MTEP14 | B | Central | AmerenIL | Decatur Route 51 138-12.47 kV Substation Terminal Upgrade | Replace 1200 A terminal equipment to 2000 A continuous current carrying capability. Upgrade bus conductor to minimum of 2000 A summer emergency capability. | 2017-06-01 | 2017-06-01 | 1132673 | Upgrade related to nearby MVP project. Terminal loaded to 126% in 2018 summer for the outage of Mt. Zion PPG-Mt. Zion Route 121 138 kV line out and Clinton generation offline. | 2016-11-01 | None | IL | IL | Planned |  |  |  | 138 | 0 | 0 | 0 | 2 | Y | AMRN43 | Ameren Services Company | Bottom-Up | Validated
4489 | 2014-12-17 | B in MTEP14 | B | Central | AmerenIL | Fargo-Pioneer 138 kV Line 1347 Rebuild | Rebuild line between Fargo and Radnor. Tentative 1600 A summer emergency target rating. | 2018-11-15 | 2018-11-15 | 3000000 | Upgrade related to nearby MVP project. Line is loaded to 107% in 2018 summer for Tazewell-Cat Sub 2 138 kV line out with Edwards #2 offline. Overload is greater with Galesburg-Fargo 345 kV MVP line completed. | 2018-11-15 | None | IL | IL | Proposed |  |  |  | 138 | 0 | 0 | 3 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
4484 | 2014-12-17 | B in MTEP14 | B | Central | AmerenMO | Hannibal, West-Palmyra-2 161 kV Line Clearance | Increase ground clearance on 9.2 miles of 795 kcmil ACSR conductor to permit operation at 120 degrees C. | 2018-11-15 | 2018-11-15 | 8547000 | Upgrade due to review of field conditions | 2018-11-15 | None | MO | MO | Proposed |  |  |  | 161 | 0 | 0 | 9.2 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
4498 | 2014-12-17 | B in MTEP14 | B | Central | AmerenMO | Berntie-Jim Hill 161 kV Line | Construct approximately 20 miles of 161 kV line between Jim Hill Plant and Berntie Substation in southeast, Missouri. The new line should have a 2000 A summer emergency rating. Construct 161 kV ring bus at Berntie Substation. Install 161 kV breaker at Jim Hill. | 2020-06-01 | 2020-06-01 | 30500000 | Improvement of reliability to local area. | 2020-06-01 | None | MO | MO | Proposed |  |  |  | 161 | 0 | 20 | 0 | 3 | Y | AMRN45 | Ameren Services Company | Bottom-Up | Validated
1795 | 2014-12-17 | B in MTEP14 | B | East | METC | David Jct. - Bingham 138kV | Rebuild approximately 19 miles of 336.4 ACSR utilizing 954 ACSR on new 138 kV future double circuit structures. | 2016-12-31 | 2016-12-31 | 19000000 | Projected to overload for various shutdown-plus-contingencies involving the Nelson Road - Murphy 345 kV circuit. | 2016-12-31 | Rebuild 19 of 336.4 ACSR utilizing 954 ACSR on new single circuit 138 kV structures. | MI | MI | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 19 | 1 | Y | METC_13_037 | METC | Bottom-Up | Validated
3922 | 2014-12-17 | B in MTEP14 | B | East | METC | Alpine J - Rogue River J - Cannon J 138kV Rebuild | Rebuild 8.4 miles of 336 ACSR utilizing 954 ACSR on new 138 kV structures. | 2016-12-31 | 2016-12-31 | 8200000 | Projected to overload for shutdown-plus-contingencies involving the Vergennes to Marquette and Vergennes to North Belding 138kV circuits. | 2016-12-31 |  | MI | MI | M1_Final SPM or OOC | BaseRel | Not Shared |  | 138 | 0 | 0 | 8.4 | 1 | Y | METC_13_039 | METC | Bottom-Up | Validated
4510 | 2014-12-17 | B in MTEP14 | B | East | METC | Morrow - Battle Creek 138kV #1 Rebuild | Rebuild approximately 22 miles of Morrow to Battle Creek 138kV #1 to 954 ACSR. Upgrade station equipment at Morrow. | 2017-12-31 | 2017-12-31 | 24640000 | Thermal overloads projected for loss of Argenta - Battle Creek 345 kV. The circuit is limited by 880-Amp Sag Limit, 477 & 4/0 CU conductors, as well as station equipment at Morrow. | 2017-12-31 |  | MI | MI | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 22 | 2 | Y | METC_13_044 | METC | Bottom-Up | Validated
4511 | 2014-12-17 | B in MTEP14 | B | East | METC | Verona-Foundry 138 kV Rebuild | Rebuild approximately 21 miles of Verona to Foundry 138kV to 1431 ACSR. Upgrade station equipment at Verona. | 2017-12-31 | 2017-12-31 | 16021000 | Thermal overloads projected for system normal conditions. The circuit is limited by 336 ACSR conductor and station equipment at Verona. | 2017-12-31 |  | MI | MI | Proposed | BaseRel | Not Shared |  | 138 | 0 | 0 | 21 | 2 | Y | METC_13_046 | METC | Bottom-Up | Validated
4603 | 2014-12-17 | B in MTEP14 | B | South | Entergy-LA | McManus to Brady Heights - Upgrade 69 kV line | Upgrade the McManus to Brady Heights 69 kV line to achieve a minimum rating of 69 MVA | 2023-12-01 | 2023-12-01 | 3319814 | The radially configured McManus to Brady Heights 69 kV line section (line 344) will exceed it's thermal rating with P1-2 event contigency loss of Port Hudson to Sandy Creek and Gravel Ridge to Jackson 69 kV lines in 2023 winter. | 2023-12-01 | None | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 4.98 | 1 | Y | 12-EGL-004 | Entergy | Bottom-Up | Validated
4608 | 2015-09-11 | B in MTEP14 | B | South | Entergy-LA | Five Points to Line Tap 281 to Line 247 Tap- Upgrade 69 kV line | Upgrade the existing Five Points to Line Tap 281 to Line 247 Tap 69 kV line sections to a minimum of 105 MVA | 2020-12-01 | 2020-12-01 | 5600000 | Loss of the existing 138-69 kV autotransformer at Moril will result in the Five Points to Line 281 tap to Line 247 tap 69 kV lines to overload. Also, a 69 kV open breaker at Moril on the LeBlanc 69 kV line will result in the line to overload. | 2020-12-01 | None | LA | LA | Proposed |  |  |  | 69 | 0 | 0 | 5.25 | 2 | Y | 11-EGL-017 | Entergy | Bottom-Up | Validated
4613 | 2015-04-03 | B in MTEP14 | B | South | Entergy-MS | Breakers at Hollandale and Belzoni (close normally-open point) | Install breakers in the Hollandale substation and build a new breaker switching station at or near the Belzoni Tap switch or Midnight substation such that the normally open line segment between the Belzoni Tap Switch and the Murphy switching station can be closed in without creating a four-terminal line | 2019-06-01 | 2019-06-01 | 10650000 | The Greenville-Rolling Fork-N.Vicksburg 115kV line is 82 miles long. The Indianola-Yazoo City 115kV line is 51 miles long. There is a normally open line segment that connects these two lines between the Hollandale and Belzoni substations. Under several N-1 contingencies, including the loss of either end of the Greenville-Rolling Fork-N.Vicksburg line or the loss of the Indianola end of the Indianola-Yazoo City line, some substations along these lines have low voltages (below 92%) and several of the Greenville - SE Greenville line segments overload. | 2019-06-01 | Installing a 230/115kV auto at Hollandale where the Clinton Industrial-Gerald Andrus 230kV line crosses the Greenville-Rolling Fork line. | MS | MS | Proposed | BaseRel |  |  | 115 | 0 | 0 | 0 | 2 | Y | 11-EMI-007 | Entergy | Bottom-Up | Validated
4439 | 2015-04-03 | B in MTEP14 | B | South | SMEPA | Plant Morrow to Purvis Bulk 161kV Line | Tap existing Purvis to Lumberton 161kV line. Construct a 161kV switching station with 3 breakers at Tap Point (new). Construct a 3 mile 161kV line from the Tap point to Morrow (new). Uprate existing line section from Purvis to Tap Point to Lumberton to 296 MVA. Add 161kV breaker at Morrow (new) | 2021-06-01 | 2021-06-01 | 3498200 | The primary need for transmission system improvements in this area is due to the need to increase transfer capability with neighboring interconnected utilities to maintain target export transfer levels. SMEPA's current tie with SOCO is at the Purvis Bulk 230/161kV transformers. During transfer analysis, the existing 2 circuits from Plant Morrow (400 MW generation station) and Purvis Bulk 161kV station would overload. By providing an additional path from Plant Morrow to Purvis Bulk station, transfer capacity was increased. | 2026-06-01 | Alternative 1: Rebuild existing Purvis Bulk - Morrow circuits 1 and 2 161kV lines with a high temperature ACCC conductor manufactured by 3M. Cost and extensive transmission modifications excluded this project from the preferred option. Alternative 2: Construct a new Plant Morrow - Lumberton 161 transmission line. This option required the most right-of-way acquisition and had the longest construction time. Alternative 3: Rebuild the existing Purvis Bulk - Morrow circuits 1 and 2 161kV lines with a two-bundled 795kcmil conductor configuration. Cost and extensive transmission modifications excluded this project from the preferred option. | MS | MS | Conceptual | Other |  | Reliability | 161 | 0 | 6 | 1 | 5 | Y | LRTPS11-RP2102 | South Mississippi Electric Power Association | Bottom-Up | Validated
4440 | 2015-04-03 | B in MTEP14 | B | South | SMEPA | Lumberton-Wiggins-Benndale 161kV Conversion | Rebuild line 35A, 37A, 37B and 37C @ 161kV insulation (new). Add 161kV breaker at Lumberton and Benndale 161kV stations (new). Construct a new Stillmore and Big Level switching station with 3 breakers (new). Construct a 8 mile line to Stillmore (new). Convert Stillmore and Big Level distribution stations to 161kV | 2021-06-01 | 2021-06-01 | 15755800 | This project was recommended by the 2002 LRTPS to solve low voltage and thermal issues on the existing Lumberton to Benndale 69kV loop. If an outage occurs on either end of the loop, such as the loss of Lumberton - Maxie or Benndale to Big Level 69kV lines, the line section would then become a radial line of considerable length with several loads being served. This would result in the adjacent section of the line overloading as well as stations along the radial experiencing low voltage. The preferred option identified by SMEPA's 2002 LRTPS recommended this project be built in Phases. This is the final phase of the project which will convert the 69kV loop to 161kV operation. | 2021-06-01 | Alternative 1: Construct a new 161kV line between Benndale and Wiggins GOAB. A new 161/69kV substation is required at Wiggins GOAB. This option required the least amount of new line construction; however, the southeastern portion of SMEPA's system would be fed primarily from Power South's transmission system during the outage of the Hintonville-Benndale 161kV. Alternative 2: Same as the Preferred Option, except this option did not recommend the installation of a 3.6 MVAR cap bank at Stillmore to postpone the need to rebuild Lumberton to Maxie 69kV line; therefore, this option was deemed to not be as cost effective. Alternative 3: Construct a new double circuit 161kV and 69kV line between Benndale and Wiggins GOAB and Lumberton. A new 161/69kV substation is required at Wiggins GOAB. This alternative was not selected as the preferred option because a single contingency would take out the double circuit 161kV and 69kV lines. | MS | MS | Conceptual | BaseRel |  |  | 161 | 0 | 16 | 17.02 | 11 | Y | LRTPS11-RP2106 | South Mississippi Electric Power Association | Bottom-Up | Validated
4441 | 2015-04-03 | B in MTEP14 | B | South | SMEPA | State Line 161kV Source Project | Tap existing Waynesboro to Hintonville 161kV line. Construct a 161kV switching station with 3 breakers at Tap Point (new). Construct a 161kV switch yard at State Line with breakers (new). Construct a 19 mile 161kV line from Tap point to State Line 161kV station (new). Add a 161/69kV 100MVA transformer at State Line (new). Add 69kV bay and breaker at State Line 69kV station (new). | 2026-06-01 | 2026-06-01 | 14250000 | The primary need for transmission system improvements in this area are due to low voltage and thermal overloads around the State Line area during the contingencies of Leakesville - Southeast Greene 69kV line, Little Rock GOAB - Clara 69kV line and Hintonville - Brown Lee Road GOAB 69kV line. Also reduces loading on the Hintonville 161/69kV transformers. | 2026-06-01 | Alternative 1: Construct a new 69kV transmission line from Plantation Pipeline to Leakesville 69kV substations, replacing the existing Hintonville 161/69kV auto transformers with 112MVA transformers and rebuilding the existing Southeast Greene - Leakesville 69kV line to 161kV specifications. This alternative was not selected as the preferred option because in order to complete the 161kV conversion project, future improvements beyond 2031 include transmission rebuilds, delivery point conversion, and a new 161/69kV substation which would cause this alternative to become more expensive than the preferred option. Alternative 2: Rebuild the Southeast Greene - Leakesville 69kV line and Hintonville - Brown Lee Road GOAB 69kV line as well as replace the Hintonville 161/69kV transformers with 112MVA transformers. This alternative was not selected as the preferred option because in order to complete the 161kV conversion project, future improvements beyond 2031 include transmission rebuilds, delivery point conversion, and a new 161/69kV substation which would cause this alternative to become more expensive than the preferred option. | MS | MS | Conceptual | BaseRel |  |  | 161 | 69 | 38 | 0 | 8 | Y | LRTPS11-RP2607 | South Mississippi Electric Power Association | Bottom-Up | Validated
3832 | 2015-05-07 | B in MTEP14 | B | West | ATC, MP | Iron Range - Arrowhead 345 kV Line | Blackberry-Arrowhead 345kV double circuit | 2025-12-31 | 2025-12-31 | 220481656.22 | Manitoba Hydro Synergy Study East option | 2025-12-31 | Manitoba Hydro Synergy Study West option | MN | MN | Proposed |  |  |  | 500 | 345 | 120 | 0 | 4 | Y | Iron Range - Arrowhead 345 kV | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
4376 | 2016-06-30 | B in MTEP14 | B | West | GRE | Parkwood-Crooked Lake 115 kV Reconductor | Reconductor the existing conductor to 795 ACSS | 2020-04-29 | 2020-04-29 | 500000 | line overloads 795 ACSR conductor | 2020-04-29 | none | MN | MN | Proposed |  |  |  | 115 | 0 | 0 | 3.36 | 1 | Y | 202496 | Great River Energy | Bottom-Up | Validated
3082 | 2014-12-17 | B in MTEP14 | B | West | MDU | NW Bismarck Ring Bus | Install 115kV ring bus at the NW Bismarck substation | 2017-06-01 | 2017-06-01 | 3050000 | Reduce transmission line exposure to distribution substations | 2017-06-01 |  | ND | ND | Planned | TBD |  |  | 115 | 0 | 0 | 0 | 1 | Y | NW Bism | Montana-Dakota Utilities Company | Bottom-Up | Validated
2548 | 2014-12-17 | B in MTEP14 | B | West | MP | Duluth 230 kV Project | Add a second 230/115 kV transformer and upgrade an existing line to 230 kV | 2026-12-31 | 2026-12-31 | 6000000 | Reliability and Load Growth in the Duluth area. Load serving capability for the Duluth area during a maintenance outage of one of the Arrowhead 230/115 kV transformers. |  |  | MN | MN | Proposed |  |  |  | 230 | 115 | 0 | 9 | 2 | Y | Duluth 230 kV Project | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
3856 | 2015-06-10 | B in MTEP14 | B | West | MP | HVDC 750 MW Upgrade | Upgrade existing HVDC line & terminal from Square Butte-Arrowhead to 750MW | 2020-12-31 | 2020-12-31 | 200000000 | Regional Transfer Capability, Regional Reliability, Market Congestion mitigation | 2020-12-31 | Project 4295: "HVDC Valve Hall Replacement" includes valve hall replacement for 550 MW transfer capability only | ND,MN | MN | Proposed |  |  |  | 250 | 230 | 0 | 465 | 7 | Y | HVDC 750 MW | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
4232 | 2014-09-18 | B in MTEP14 | B | West | MPC, OTP | Winger-Thief River Falls 230 kV Line | Winger Sub Expansion, Thief River Sub Expansion, New 47 mile 230kV Transmission Line Between Winger & Thief River, Thief River 230/115 Transformer | 2024-11-15 | 2024-11-15 | 28000000 | Support Load Growtth in North West Minnesota with a new 230 kV source - Project back to MTEP B Actual load growth has not matched modeled load growth at this time. Moving this project back into Appendix B in Portal & MOD & moving the in service date out to 2024 due to the actual load growth on the system. | 2024-11-15 | Donaldson-Drayton 115 kV Line #2, Grand Forks-Falconer 115 KV #2, Winger-Plummer 115 kV #2, Lake Ardoch-Thief River 230 kV; Lake Ardoch 230/115 kV Sub | MN | MN | Proposed | BaseRel |  |  | 230 | 115 | 47 | 0 | 4 | Y | OTP, MPC | Otter Tail Power Company | Bottom-Up | Validated
2995 | 2014-10-01 | B in MTEP15 | B | Central | AmerenIL | Brokaw Substation Bus Conductor Replacment | Brokaw 345/138 kV Substation - Replace 477 kcmil ACSR Bus Conductor in Brokaw-Normal East 138 kV Line 1578 position with conductor capable of carrying 1200 A continuously. | 2017-06-01 | 2017-06-01 | 100000 | C1: S. Bloomington West Bus outage, 105% in 2018 summer |  |  | IL | IL | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 | Y |  | Ameren Services Company | Bottom-Up | Validated
3010 | 2015-03-19 | B in MTEP15 | B | Central | AmerenIL | Baldwin-Grand Tower-N.W. Cape (Heritage) 345 kV Line | New 69 mile, single-circuit line (possible double circuit), 3000 A SE capability (Baldwin-Grand Tower - 45 miles; Grand Tower-N.W. Cape - 24 miles). Grand Tower 345/138 kV Substation - 1-560 MVA transformer, 345 kV Ring bus | 2030-06-01 | 2030-06-01 | 5000000 | Relief for St. Francois-Lutesville. |  |  | IL | IL | Proposed | Other |  | Reliability | 345 | 138 | 69 | 0 | 2 | Y | AMRN13 | Ameren Services Company | Bottom-Up | Validated
7801 | 2015-09-11 | B in MTEP15 | B | Central | AmerenIL | Cahokia-Ashley-2 138 kV Reconductoring | Reconductor 2.6 miles of parallel 350 kcmil copper conductor with conductor capable of carrying 2000 A under summer emergency conditions. | 2018-06-01 | 2018-06-01 | 0 | For the outge of the Prairie State-Stallings-4531 and Cahokia-Roxford-4 345 kV lines, the existing conductor would be loaded to 131% in 2020 summer. | 2018-06-01 |  | MO,IL | MO,IL | Proposed | BaseRel |  |  | 138 | 0 | 0 | 2.6 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7802 | 2015-11-24 | B in MTEP15 | B | Central | AmerenIL | West Frankfort, East-West-Frankfort-1 138 kV Reconductoring | Reconductor 5.25 miles of 1272 kcmil ACSR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace bus conductor at West Frankfort, East with conductor having capability equal to or greater than the new line conductor. | 2026-06-01 | 2026-06-01 | 0 | During light load conditions in 2018, this line would be loaded to 106% of its 308 MVA summer emergency rating following an outage to the Mt. Vernon-East West Frankfort 345 kV line, with Joppa Unit #2 offline, based on 2013 analysis. | 2026-06-01 |  | IL | IL | Proposed | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7821 | 2016-06-02 | B in MTEP15 | B | Central | AmerenIL | Kickapoo Capacitor Bank Addition | Install --2-7.2 Mvar, 34.5 kV capacitor banks and PCBs. | 2020-06-01 | 2020-06-01 | 0 | Voltage support needed (Kickapoo 138 kV at 93% in 2018 summer) for the outage of the Fogarty-Kickapoo 138 kV line with Edwards Unit #3 offline, based on 2013 analysis. | 2020-06-01 |  | IL | IL | Proposed | BaseRel |  |  | 34.5 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7826 | 2015-03-19 | B in MTEP15 | B | Central | AmerenIL | Turkey Hill 138 kV Bus-Tie Breaker | Install 138 kV bus tie breaker. Needed: 1-138 kV, 2000 A (minimum), 40 kA PCB. | 2019-12-01 | 2019-12-01 | 0 | Increased reliability | 2019-12-01 |  | IL | IL | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7861 | 2015-03-19 | B in MTEP15 | B | Central | AmerenIL | Effingham Northwest Breaker Additions | Install 2-138 kV, 2000 A, 40 kA PCBs, one on each 138 kV line position. Upgrade bus conductor to 2000 A continuous capability. | 2019-06-01 | 2019-06-01 | 0 | Increased reliability | 2019-06-01 |  | IL | IL | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7863 | 2015-03-19 | B in MTEP15 | B | Central | AmerenIL | Tilden Substation 138 kV Ring Bus | Establish a 5 position 138 kV ring bus for 4-138 kV lines and 1-138/34.5 kV transformer. | 2020-12-01 | 2020-12-01 | 0 | Increased reliability | 2020-12-01 |  | IL | IL | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7870 | 2015-09-11 | B in MTEP15 | B | Central | AmerenIL | Brokaw Substation 138-69 kV Xfmr Connection | Connect 138-69 kV Transformer to 138 kV bus at Brokaw Substation. | 2019-05-01 | 2019-05-01 | 0 | Local load serving need | 2019-05-01 |  | IL | IL | Proposed | Other |  | Reliability | 138 | 69 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
7862 | 2014-12-05 | B in MTEP15 | B | Central | AmerenMO | Buick Smelter Substation Relocation | Relocate substation. Remove existing substation, install 2 motor-operated 161 kV switches and 2 customer owned and installed 161 kV circuit switchers. Make provisions for the addition of a third 161-4 kV transformer. | 2016-12-01 | 2016-12-01 | 0 | Condition of existing structures | 2016-12-01 |  | MO | MO | Proposed | Other |  | Condition | 161 | 4 | 0 | 0 | 1 |  |  | Ameren Services Company | Bottom-Up | Validated
3440 | 2014-09-16 | B in MTEP15 | B | Central | BREC | Reid EHV 161/69 kV transformer | Add a 56 MVA transformer to the existing Reid EHV substation. | 2024-12-31 | 2024-12-31 | 5000000 | Overload with loss of one Reid 161/69 kV transformer. | 2018-12-31 | Add third 161/69 kV transformer at Reid Switchyard. | KY | KY | Proposed | BaseRel | Not Shared |  | 161 | 69 | 0 | 0 | 1 | Y | LRP6 | Big Rivers Electric Corporation | Bottom-Up | Validated
7888 | 2015-04-28 | B in MTEP15 | B | Central | PPI | Tyson 161/69 kV substation and 69 kV lines | Project Modified from original submittal and moved to Appendix B. Tyson substation is no longer part of this project. 69 kV terminal addition at MidAmerican Sub 39. Construct new 11 mile 69 kV line from MidAmerican Sub 39 to PPI/Jo-Carroll Energy Ladwig Substation. Construct 0.2 mile 69 kV line from the City of Geneseo plant to Jo-Carroll Energy Geneseo Substation. | 2016-12-31 | 2016-12-31 | 289300 | Jo-Carroll Energy's Ladwig and Geneseo distribution substations are presently at the end of a long radial 34.5 kV line served from Ameren's Atkinson delivery point which in turn is served from the 138/34.5 kV East Kewanee substation. Ladwig is 36.8 miles from East Kewanee and JCE Geneseo is 28.9 miles from East Kewanee. Also, the City of Geneseo, IL is served via a radial 69 kV line sourced from MEC's Sub 39. This project will provide a new 69 kV source and associated 69 kV lines to allow the networking of both the Geneseo municipal system and the JCE Ladwig and Geneseo substations. | 2016-12-31 |  | IL | IL | Proposed | Other |  | Reliability | 69 | 69 | 0.2 | 7.62 | 3 |  | 2015-19,20,41 | Prairie Power, Inc. | Bottom-Up | Validated
4394 | 2014-10-06 | B in MTEP15 | B | Central | Vectren | Grandview 138/69 kV Transformer Upgrade | Replace the 60 MVA transformer at Grandview with a 100 MVA | 2019-12-31 | 2019-12-31 | 1500000 | Future year studies show higher and higher post contingent loadings and several post contingent overloads | 2019-12-31 | Install a 2nd 138/69 kV transformer | IN | IN | Planned |  |  |  | 138 | 69 | 0 | 0 | 1 | Y | 2013SIGE8 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4395 | 2014-10-06 | B in MTEP15 | B | Central | Vectren | NE cap bank tertiary conversion | Remove existing cap banks from the tertiary winding of the 138/69 kV transformer at Northeast sub, and install equivalent cap banks on the 69 kV bus with breakers | 2019-12-31 | 2019-12-31 | 450000 | To remove old cap banks from the transformer tertiary winding | 2019-12-31 | None | IN | IN | Planned |  |  |  | 69 | 0 | 0 | 0 | 1 | Y | 2013SIGE9 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4396 | 2016-05-18 | B in MTEP15 | B | Central | Vectren | Z71 Scott - Toyota | Install new approx. 13 mile 138 kV line designate Z71 (not Z75). | 2020-12-31 | 2020-12-31 | 13000000 | 138 kV line designate Z71 (not Z75). Provide another 138 kV feed to a large customer (Toyota), provide another path for post contingent flows through the Francisco 345/138 transformer and 138 kV line from Francisco - Elliott (a top congested flowgate), and to provide additional post-continge | 2020-12-31 |  | IN | IN | Planned |  |  |  | 138 | 0 | 13 | 0 | 1 | Y | 2013SIGE10 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4397 | 2014-10-06 | B in MTEP15 | B | Central | Vectren | Y31 Leonard Rd. - Z93 Rebuild | Rebuild approx. 6.8 miles of 69 kV | 2020-12-31 | 2020-12-31 | 5100000 | Aging Infrastructure. | 2020-12-31 |  | IN | IN | Planned |  |  |  | 69 | 0 | 0 | 6.78 | 1 | Y | 2013SIGE11 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4398 | 2014-10-06 | B in MTEP15 | B | Central | Vectren | Y52-1 NE - Sunbeam Rebuild | Rebuild and reconductor approx. 3 miles of 69 kV | 2021-12-31 | 2021-12-31 | 2250000 | Aging Infrastructure. | 2021-12-31 |  | IN | IN | Planned |  |  |  | 69 | 0 | 0 | 2.95 | 1 | Y | 2013SIGE12 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4399 | 2016-05-19 | B in MTEP15 | B | Central | Vectren | Newtonville 161 kV ring bus conversion | Convert existing 161 kV bus to a ring bus configuration | 2023-12-31 | 2023-12-31 | 1000000 | Increased reliability on existing 161 kV bus. Currently the loss of T3 causes the loss of the 161 kV line to Coleman (the loss of the line to Coleman also causes the loss of T3), and the loss of T5 causes the loss of the 161 kV line to Troy (the loss of | 2023-12-31 |  | IN | IN | Planned |  |  |  | 161 | 0 | 0 | 0 | 1 | Y | 2013SIGE13 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | Bottom-Up | Validated
4520 | 2015-04-22 | B in MTEP15 | B | East | ITCT | Mortar Creek (formerly Hull Road) Station | Build Mortar Creek 345 kV station and reconfigure the Bayshore to Monroe 345 kV, Lemoyne to Majestic 345 kV, and Morocco to Milan to Monroe 345 kV lines into it in a breaker-and-a-half scheme configuration. | 2018-06-01 | 2018-06-01 | 23950000 | Reduce loading on the conductors of the Brownstown - Monroe 1 345 kV, and Monroe - Wayne 345 kV. | 2018-06-01 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 0 | 0 | 0 | 9 | Y | ITC_14_001 | ITC Transmission | Bottom-Up | Validated
3943 | 2014-12-02 | B in MTEP15 | B | East | ITCT | Navarre 230/120 kV Transformer #201 | Increase the CT ratio on the low-side breaker of the Navarre 230/120 kV Transformer #201. | 2018-12-31 | 2018-12-31 | 0 | Projected to overload for the shutdown plus contingency involving the DIG M to Navarre to Waterman 230 kV circuit and the Waterman 230/120 kV transformer. | 2018-12-31 |  | MI | MI | Proposed |  |  |  | 230 | 120 | 0 | 0 | 1 | Y |  | ITC Transmission | Bottom-Up | Validated
8068 | 2015-04-22 | B in MTEP15 | B | East | ITCT | Brownstown - Monroe #2 345 kV Sag Remediation | Remediate the sag limit on the Brownstown to Monroe #2 345 kV line | 2017-12-31 | 2017-12-31 | 1200000 | The Brownstown to Monroe #2 345 kV line is projected to become overloaded with the proposed Mortar Creek 345 kV station (see Midcontinent ISO Project ID# 4520) in-service for shutdown plus contingency scenarios involving the Brownstown to Monroe 1 345 kV line and either the Fermi 2 generation or the Monroe to Wayne 345 kV line. | 2017-12-31 |  | MI | MI | Planned | Other |  | Reliability | 345 | 0 | 0 | 18.2 | 1 |  | ITC_13_061 | ITC Transmission | Bottom-Up | Validated
8069 | 2015-04-22 | B in MTEP15 | B | East | ITCT | Lemoyne - Majestic 345 kV Sag Remediation | Remediate the sag limit on the Lemoyne - Majestic 345 kV line to increase its summer emergency rating to a minimum rating of 1822 MVA / 3049 Amps. | 2018-12-31 | 2018-12-31 | 2500000 | The Lemoyne - Majestic 345 kV circuit overloads for shutdown plus contingency scenarios involving the Morocco - Allen Junction 345 kV and Bayshore - Monroe 345 kV lines. The loading on the newly created Lemoyne to Mortar Creek 345 kV line is expected to be substantially higher (See Project ID# 4520). | 2017-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 0 | 0 | 0 | 1 |  | ITC_13_056 | ITC Transmission | Bottom-Up | Validated
8099 | 2015-04-22 | B in MTEP15 | B | East | ITCT | Lincoln to Northeast/Northwest 120 kV Rebuild | Rebuild about 2.95 miles of 477 ACSR on the Lincoln section of the Lincoln/Northeast/Northwest circuit to 1431 ACSR on new 120 kV double circuit towers. The other side of these towers supports a portion of the Lincoln to Northeast 120 kV circuit which will also be upgraded to 1431 ACSR. Upgrades or replacement of any limiting equipment at Lincoln, Hilton Road (formerly Ferndale), and Northeast substations will also be necessary. | 2018-12-31 | 2018-12-31 | 4200000 | The Lincoln section of the Lincoln-Northeast-Northwest 120 kV circuit is projected to overload under various shutdown plus contingency scenarios, the worst involving the loss of Chestnut to Red Run 120 kV and Ferndale to Northeast 120 kV circuits. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 120 | 0 | 0 | 0 | 2 |  | ITC_14_014 | ITC Transmission | Bottom-Up | Validated
1804 | 2014-12-02 | B in MTEP15 | B | East | METC | Marquette - Easton Jct. 138kV | Replace limiting equipment at the Marquette 138 kV station | 2018-12-31 | 2018-12-31 | 0 | Relieve projected contingency overload on Marquette-Easton Jct. | 2018-12-31 |  | MI | MI | Proposed |  |  |  | 138 | 0 | 0 | 0 | 1 | Y |  | METC | Bottom-Up | Validated
3927 | 2015-07-22 | B in MTEP15 | B | East | METC | Saginaw River 138 kV Station Equipment Replacement | Replace limiting equipment from the Saginaw River 138 kV station. | 2017-12-31 | 2017-12-31 | 2800000 | Station equipment at Saginaw River is projected to overload during the shutdown plus contingency scenario involving the loss of the Karn to Manning 138 kV and Atlanta - Karn - Thetford 138 kV circuits. | 2017-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 138 | 0 | 0 | 0 | 1 | Y | METC_14_026 | METC | Bottom-Up | Validated
4525 | 2015-04-22 | B in MTEP15 | B | East | METC | Goss 345/138 kV Transformer #2 | Install a second 345/138 kV transformer and install/upgrade station equipment at Goss. | 2018-12-31 | 2018-12-31 | 9300000 | The Goss 345/138 kV transformer is projected to overload in a shutdown-plus-contingency that takes out Goss - Thetford and Murphy - Nelson Road 345 kV lines. | 2018-12-31 |  | MI | MI | Planned | Other |  | Reliability | 345 | 138 | 0 | 0 | 2 | Y | METC_14_015 | METC | Bottom-Up | Validated
8123 | 2015-04-22 | B in MTEP15 | B | East | METC | Weeds Lake Transformer #2 and Looping in Argenta to Twin Branch 345 kV | Install a second 345/138 kV transformer at the Weeds Lake Substation and loop in the Argenta to Twin Branch 345 kV line. This creates a Weeds Lake - Twin Branch 345 kV line and a 2nd Argenta - Weeds Lake 345 kV circuit | 2018-12-31 | 2018-12-31 | 17500000 | Weeds Lake Transformer #1 is projected to overload for single and double contingencies involving the Argenta - Weeds Lake 345 kV-1 circuit. Overloads are shown to occur in shoulder peak and 70% peak load cases with flow out and zero flow across the ITCT/IESO interface in the 2014 ITCTransmission/METC Near Term (2019) Assessment. | 2018-12-31 |  | MI | MI | Proposed | Other |  | Reliability | 345 | 138 | 0.2 | 0 | 5 |  | METC_14_028 | METC | Bottom-Up | Validated
8130 | 2015-04-22 | B in MTEP15 | B | East | METC | Pere Marquette to Keystone 230 kV | Construct a new 75 mile, 230 kV circuit between Keystone and Pere Marquette Substation. Approx. 20 miles of the new line will be on new double circuit steel pole structures, 30 miles from rebuiding existing 138 kV structures to 230 kV double circuit steel poles, and 25 miles on existing DCTs with a vacant side of the structures. Install a 345/230 kV transformer and associated terminal equipment at Pere Marquette substation. Add a 230/138 kV transformer and associated terminal equipment at Keystone substation. Project will also swap the line positions of the Keystone-Wexford 138 kV and the 138 kV side of the Keystone 345/138 kV transformer at Keystone substation. | 2018-12-31 | 2018-12-31 | 90198000 | The shutdown-plus-contingency combination of the Keystone to Ludington and Tittabawassee to Gallagher to Livingston 345 kV lines causes voltage violations. During maintenance conditions when one of the two 345 kV circuits (Keystone to Ludington 345 kV or Tittabawassee to Gallagher to Livingston 345 kV) is shutdown and the second 345 kV is forced out, a large part of northern Michigan was projected to experience widespread low voltages TheTippy ? Wexford 138 kV line is projected to be overloaded for the T-1-1 scenario that takes out both the Keystone ? Ludington 345 kV and the Keystone ? Tippy 138 kV circuits. | 2018-12-31 |  | MI | MI | Proposed | BaseRel |  |  | 345 | 138 | 46.4 | 29.4 | 5 |  | METC_13_049 | METC | Bottom-Up | Validated
7905 | 2016-01-12 | B in MTEP15 |  | East | MPPA | Traverse City South Substation | Traverse City is building a new 69 kV distribution substation as well as reconductoring all lines around the Traverse City system. This substation will be along the Grand Traverse to East Hammond line. |  |  |  | The project is driven by needs on the distribution system. However there are benefits to the 69kV system due to the station placement. 1. Eliminates a radial tap to the Wolverine Power, South Airport Substation. 2. Provides better switching (breakers in place of 69kV line switches) for the TCLP system. 3. Provides greater reliability for TCLP and WPSC customers due to separating the former Grand Traverse to East Hammond line into two sections. Fewer substations will be affected due to a 69kV line operation/outage. | [10 empty] | #N/A | #N/A | #N/A |  |  | Michigan Public Power Agency | Bottom-Up | Validated
8026 | 2014-12-01 | B in MTEP15 | B | East | NIPS | Dekalb Transformer | Upgrade Dekalb 138/69kV Transformer. This will also increase ratings of the Dekalb to Auburn 138kV Line | 2017-12-31 | 2017-12-31 | 2700000 | Age & Condition only. Risk of overload for a C2(common breaker failure)- See Comments. |  | Alternative Project for C2 - Lagrange Bus tie Mitigation: Lagrange 138kV Ring Bus. | IN | IN | Planned |  |  |  | 138 | 69 | 0 | 0 | 2 |  |  | Northern Indiana Public Service Company | Bottom-Up | Validated
8360 | 2015-03-30 | B in MTEP15 | B | East | WPSC | Alba New Station | The Alba transmission tie station represents the oldest tie on the Wolverine system. It is located on a small parcel of leased property with limited expansion capability. The existing station shall be replaced with a new in/out transmission line design, three (3) breaker substation, modern control house, metering, protection relaying and a 50 or 90MVA, 138/69kV tie transformer, dependent upon load requirements. | 2021-12-31 | 2021-12-31 | 4000000 | Rebuild old substation and improve 138kV protection with new 138KV breaker station. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Condition | 138 | 69 | 0 | 0 | 1 |  | Alba New Station | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Validated
8361 | 2015-03-30 | B in MTEP15 | B | East | WPSC | Alba Line Mods | This project will address 138kV transmission line and structure reconfiguration costs associated with construction of the new Alba transmission substation, so that the 138kV ITC/METC looped transmission line segments can successfully enter and leave the substation | 2021-12-31 | 2021-12-31 | 1000000 | Line mods for the new Alba 138/69kV transmission substation. |  |  | MI | MI | Proposed | Other |  | Reconfig | 138 | 69 | 0 | 0 | 1 |  | Alba Line Mods | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Validated
8362 | 2015-03-30 | B in MTEP15 | B | East | WPSC | Casnovia to White Cloud Rebuild | This 69kV transmission line segment was built in 1963. This line segment has 67% condemned, rotten tops, or damaged structures. This rebuild is necessary due to the age of the line and poles. Because there are so many poles in need of replacing, it is cost-effective to demolish the existing line and rebuild to our new standard configuration | 2019-12-31 | 2019-12-31 | 11500000 | Aging Infrastructure | 2019-12-31 |  | MI | MI | Proposed | Other |  | Condition | 69 | 0 | 0 | 22.85 | 1 |  | CV-WC Rebuild | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Validated
8363 | 2015-03-30 | B in MTEP15 | B | East | WPSC | Vestaburg to Crawford Rebuild | This 69kV transmission line segment was built in 1973. This line segment has 58% condemned, rotten tops, or damaged structures. This rebuild is necessary due to the age of the line and poles. Because there are so many poles in need of replacing, it is cost-effective to demolish the existing line and rebuild to our new standard configuration. | 2019-12-31 | 2019-12-31 | 4500000 | Aging Infastructure. | 2019-12-31 |  | MI | MI | Proposed | Other |  | Condition | 69 | 0 | 0 | 9 | 1 |  | VB-CF rebuild | Wolverine Power Supply Cooperative, Inc. | Bottom-Up | Validated
7993 | 2015-04-01 | B in MTEP15 | B | South | CLECO | Rodemacher to East Leesville(reconductor) | Reconductor Rodemacher to East Leesville 230 kv line. | 2024-05-01 | 2024-05-01 | 10000000 | N1-G1 contingencies show this line overloading in the 2024 Summer Peak Case for the loss of Rodemacher to Colfax 230 kV line and Dolet Hills Generator. | 2024-05-01 |  | LA | LA | Proposed | BaseRel |  |  | 230 | 0 | 0 | 38.28 | 1 |  |  | Cleco Power LLC | Bottom-Up | Validated
7994 | 2015-04-01 | B in MTEP15 | B | South | CLECO | Westfork to Spectra 138 kV | This project Taps the Existing Plaisance to Veazie 138 kV line 2.73 miles from Veazie and creates a new 3 terminal 138 kV Substation called Spectra. In addition to this new substation a new 2.72 mile 138 kV line will be built from Westfork Substation. Also a bigger 230/138 kV Auto will be purchased at Westfork. Upon the completion of this project the Normally open point between Westfork and Guidry or Guidry to Veazie can be operated looped or normally in service. | 2015-05-01 | 2024-05-01 | 13500000 | N-1 low voltage at Guidry shows up in all the summer models for the loss of Coughlin to Plaisance 138 kV line. The Guidry load will be moved to be normally fed from Westfork in the 2015 MTEP models. After Guidry is moved voltage in the are continues to be low for the loss of Coughlin to Plaisance 138 kV line. In 2024 Summer peak the low voltage at Veazie and Plaisance exceeds Cleco Planning criteria. Additionally serving this load looped increases reliability to the City of Opelousas and provides greater flexability for maintenance outages. | 2024-05-01 |  | LA | LA | Conceptual | BaseRel |  |  | 230 | 0 | 3 | 0 | 4 |  |  | Cleco Power LLC | Bottom-Up | Validated
4664 | 2015-07-29 | B in MTEP15 | B | South | Entergy-AR | Holland Bottoms - Beebe: Build new 161kV line, Install 161/115kV auto | Rebuild the Beebe substation to include 115 kV breakers, add a 161 kV bus with breakers and install a 400 MVA 161/115 kV autotransformer. Construct a new 161 kV line from Holland Bottoms to Beebe with a minimum capacity of 360 MVA. | 2023-06-01 | 2023-06-01 | 55451500 | Loss of the Cabot to Holland Bottom 115 kV line results in low voltages along the Holland Bottoms to Searcy Price 115kV line. | 2023-06-01 | Convert existing Holland Bottoms to Searcy Price line from 115 to 161 kV | AR | AR | Proposed | BaseRel |  |  | 161 | 115 | 14.5 | 0 | 2 | Y | 14-EAI-005 | Entergy Arkansas | Bottom-Up | Validated
4626 | 2015-09-13 | B in MTEP15 | B | South | Entergy-LA | Meaux to Abbeville - Upgrade Meaux Line bay bus | Upgrade terminal equipment at Meaux to increase the rating of the line to a minimum of 251 MVA. | 2026-12-01 | 2026-12-01 | 50000 | Loss of the Moril to Delcambre 138 kV line results in the Meaux to Abbeville 138 kV line to overload | 2026-12-01 | None | LA | LA | Conceptual | BaseRel |  |  | 138 | 0 | 0 | 0 | 1 | Y | 14-EGL-010 | Entergy | Bottom-Up | Validated
7914 | 2015-04-03 | B in MTEP15 | B | South | Entergy-MS | Medical Center Solution: Constuct new 115 kV substation and upgrade 115 kV line | Construct new 115 kV breaker station on Monument Street - Fondren 115 kV line to provide second distribution load serving source to Medical Center complex. Construct new Rex Brown - NEW breaker station 115 kV utilizing the existing HICO - Fondren 115 kV line path to minimum 260 MVA. | 2017-06-01 | 2017-06-01 | 15508930 | "Distribution System Load Growth This distribution project needed to meet new substation request around Medical Center Complex in downtown Jackson, MS. NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P6 loss of Rex Brown - Monument St 115 kV circuit + loss of South Jackson 230/115 kV autotransformer results in a cascading outage event in the central Mississippi transmission network." | 2020-06-01 |  | MS | MS | Proposed | BaseRel |  |  | 115 | 0 | 5.5 | 0 | 3 |  | 15-EMI-008 | Entergy | Bottom-Up | Validated
4623 | 2015-03-31 | B in MTEP15 | B | South | Entergy-TX | Panorama to Longmire 138 kV Line: Reconductor | Reconductor approximately 2.73 miles of 138 kV line to a minimum of 468 MVA ( 1272 ACSS). The line rating will continue to be limited by the 1200 amp breaker at Longmire (287 MVA). Line Bay Bus and risers at Panorama (currently 649.5 ACAR rated at 860 amps and 1033 AAC rated at 1017 amps) will also need to be replaced to meet or exceed the conductor rating of 468 VA (1957 amps). | 2019-06-01 | 2019-06-01 | 3200000 | The Panorama to Longmire 138 kV line 596 overloads with the loss of the Grimes to Crockett 345 kV line 119 coupled with the loss of the Frontier generation | 2019-06-01 | Construct new Lewis Creek to Ponderosa 230 kV line on new ROW | TX | TX | Proposed | BaseRel |  |  | 138 | 0 | 0 | 2.73 | 2 | Y | 13-ETI-014 | Entergy | Bottom-Up | Validated
4799 | 2015-09-11 | B in MTEP15 | B | South | Entergy-TX | Dishman: Construct new substation | Construct new 230kV substation on the Amelia to Helbig 230kV line | 2021-06-01 | 2021-06-01 | 10500000 | New load serving substation | 2021-06-01 | None | TX | TX | Proposed | Other |  | Distribution | 230 | 0 | 0 | 0 | 1 | Y | 13-ETI-021 | Entergy | Bottom-Up | Validated
7916 | 2015-03-31 | B in MTEP15 | B | South | Entergy-TX | New Caney - Cut 138 kV line 571 into substation | Route 138 kv line 571 into the New Caney 138 kV bus. | 2018-06-01 | 2018-06-01 | 5000000 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Loss of the Porter to New Caney 138 kV line 586 coupled with loss of the Sabine 3 generator (P3-2) will cause the Cleveland to Tarkington 138 kV line 50 to overload. Cutting 138 kV line 571 into the New Caney substation will alleviate the contingency causing this overload. | 2018-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 138 | 0 | 0.1 | 0 | 5 |  | 15-ETI-004 | Entergy | Bottom-Up | Validated
7958 | 2015-03-31 | B in MTEP15 | B | South | Entergy-TX | Linscomb - Construct new 230 kV substation | Construct new Linscomb 230 kV substation on line 195 between the new Chisholm Road substation and Helbig. | 2018-06-01 | 2018-06-01 | 5500000 | Distribution System Load Growth This distribution project is needed to relieve distribution facility loadings in the area between McLewis and Mahew and provide service to a rapidly developing commercial and residential area. | 2018-06-01 |  | TX | TX | Proposed | Other |  | Distribution | 230 | 0 | 0.2 | 0 | 3 |  | 15-ETI-009 | Entergy | Bottom-Up | Validated
7972 | 2015-03-31 | B in MTEP15 | B | South | Entergy-TX | Upgrade Jacinto Splendora 138 kV Line | Reconductor Jacinto - Splendora 138 kV line 871. | 2023-06-01 | 2023-06-01 | 14370790 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. A thermal overload of the Jacinto to Splendora 138 kV line will occur during the N1G1 contingency (P3-2) loss of the Porter to China 230kv line coupled with the loss of the Lewis Creek Unit 1 generator. This project will increase the thermal capacity of the 138 kV transmission circuit by reconductoring the transmission line and upgrading station equipment at Jacinto and Splendora. | 2023-06-01 |  | TX | TX | Proposed | BaseRel |  |  | 138 | 0 | 0 | 13 | 2 |  | 11-ETI-039 | Entergy | Bottom-Up | Validated
8141 | 2015-04-03 | B in MTEP15 | B | South | SMEPA | Rebuild L16 (Hoy - Sharon GOAB) 69kV Line | Rebuild the existing Hoy - Sharon GOAB 69kV line using 161kV double circuit specifications and 795 ACSR conductor. | 2026-06-01 | 2026-06-01 | 1273600 | The existing Hoy-Sharon 69kV line overloads during the outage of the Ellisville Junction-Glade GOAB 69kV line. Rebuilding the line using 795 ACSR conductor with DC provisions to allow for a future 161kV line resolves the overload. | 2026-06-02 |  | MS | MS | Conceptual | BaseRel |  |  | 69 | 0 | 0 | 3.98 | 1 |  |  | South Mississippi Electric Power Association | Bottom-Up | Validated
8143 | 2015-04-03 | B in MTEP15 | B | South | SMEPA | Rebuild L45A (Foxworth - Pickwick GOAB) 69kV Line | Rebuild the existing Foxworth - Pickwick GOAB 69kV line using 161kV specifications and 795 ACSR conductor. | 2026-06-01 | 2026-06-01 | 2050300 | The existing Foxworth - Pickwick GOAB 69kV line overloads during the outage of the Lumberton - Baxterville 69kV line. Rebuilding the line using 795 ACSR conductor resolves the overload. | 2026-06-01 |  | MS | MS | Conceptual | BaseRel |  |  | 69 | 0 | 0 | 7.07 | 1 |  |  | South Mississippi Electric Power Association | Bottom-Up | Validated
1718 | 2014-09-10 | B in MTEP15 | B | West | ATC | Install Custer 138/69 kV transformer | Install a 138/69 kV transformer at Custer substation | 2022-06-01 | 2022-06-01 | 4904268 | Thermal overloading & low voltages occur under Category B conditions. | 2022-06-01 |  | WI | WI | Conceptual | Other | Not Shared | Reliability | 138 | 69 | 0 | 0 | 1 | Y | F2081 | American Transmission Co. LLC | Bottom-Up | Validated
1719 | 2014-09-10 | B in MTEP15 | B | West | ATC | Construct Shoto-Custer 138 kV line | Construct a Shoto-Custer 138 kV line | 2022-06-01 | 2022-06-01 | 22938000 | Thermal overloading & low voltages occur under Category B conditions. | 2022-06-01 |  | WI | WI | Conceptual | BaseRel | Shared |  | 138 | 0 | 9.94 | 0 | 1 | Y | F2081 | American Transmission Co. LLC | Bottom-Up | Validated
3678 | 2014-09-10 | B in MTEP15 | B | West | ATC | Construct Marquette-Mackinac 138 kV | Rebuilds Forsyth to Nine Mile as 138 kV line and rebuilds from Nine Mile to Straits area as 138 kV. This includes a new 138 kV connection between Seney and Roberts. | 2050-12-31 | 2050-12-31 | 262850000 | Reliability |  |  | MI | MI | Conceptual | Other | Not Shared | Reliability | 138 | 69 | 200 | 0 | 15 | Y | NP-Package1 | American Transmission Co. LLC | Bottom-Up | Validated
3838 | 2014-09-10 | B in MTEP15 | B | West | ATC | Construct Plains-National 345 kV | New 345 kV line from Plains to National, including new National substation and transformers | 2019-06-01 | 2050-12-31 | 180800000 | Reliability | 2016-12-31 |  | WI | MI | Conceptual | TBD | TBD |  | 345 | 138 | 60 | 0 | 5 | Y | NP Project | American Transmission Co. LLC | Bottom-Up | Validated
7580 | 2014-09-10 | B in MTEP15 | B | West | ATC | Install 138 kV Werner West Inductor | Install a 138 kV 25 Mvar inductor at Werner West | 2018-06-01 | 2018-06-01 | 1524446 | Reliability | 2018-12-31 |  | WI | WI | Conceptual |  |  |  | 138 | 0 | 0 | 0 | 1 |  | PR06427 | American Transmission Co. LLC | Bottom-Up | Validated
7581 | 2014-09-10 | B in MTEP15 | B | West | ATC | Install 138 kV Forest Jct Inductor | Install a 138 kV 25 Mvar inductor at Forest Jct | 2018-06-01 | 2018-06-01 | 1762635 | Reliability | 2018-12-31 |  | WI | WI | Conceptual |  |  |  | 138 | 0 | 0 | 0 | 1 |  | PR06425 | American Transmission Co. LLC | Bottom-Up | Validated
7584 | 2015-01-14 | B in MTEP15 | B | West | ATC | Rebuild New Holstein - St Nazianz - Custer 69 kV | Rebuild P-68 New Holstien - St Nazianz- Custer 69 kV circuit with T2-4/0 ACSR | 2022-12-31 | 2022-12-31 | 15941421 | Reliability | 2022-12-31 |  | WI | WI | Conceptual |  |  |  | 69 | 0 | 0 | 21.34 | 2 |  | PR04986 | American Transmission Co. LLC | Bottom-Up | Validated
7585 | 2014-09-18 | B in MTEP15 | B | West | ATC | Install 2nd Colley Rd 138/69 kV transformer | Add 2nd 138/69 kV transformer at Colley Rd | 2023-06-01 | 2023-06-01 | 9944381 | Reliability | 2023-12-31 |  | WI | WI | Conceptual |  |  |  | 138 | 69 | 0 | 0 | 1 |  | PR06370 | American Transmission Co. LLC | Bottom-Up | Validated
7586 | 2014-09-18 | B in MTEP15 | B | West | ATC | Atlantic 138/69 kV bus reconfiguation and transformer addition | Reconfigure the Atlantic substations 138 kV and 69 kV bus work. Denergize the existing Atlantic 138/69 kV transformer and install a new 138/69 kV transformer. | 2019-06-01 | 2019-06-01 | 9043283 | Reliability, Asset Renewal | 2019-12-31 |  | WI | WI | Conceptual |  |  |  | 138 | 69 | 0 | 0 | 12 |  | PR05856 | American Transmission Co. LLC | Bottom-Up | Validated
7600 | 2014-09-18 | B in MTEP15 | B | West | ATC | Rebuild Sheepskin - Stoughton 69 kV | Rebuild Y-12 Sheepskin to Stoughton with T2-4/0 ACSR | 2023-12-31 | 2023-12-31 | 10827858 | Reliability | 2023-12-31 |  | WI | WI | Conceptual |  |  |  | 69 | 0 | 0 | 6.46 | 1 |  | PR06459 | American Transmission Co. LLC | Bottom-Up | Validated
7762 | 2014-09-18 | B in MTEP15 | B | West | ATC | Rebuild Y-19 Wautoma - Harrison 69 kV | Rebuild Y-19 from Wautoma to Harrison 69 kV with T2 4/0 Penguin conductor. | 2023-12-31 | 2023-12-31 | 0 | Reliability | 2023-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 30.78 | 6 |  | PR06460 | American Transmission Co. LLC | Bottom-Up | Validated
7763 | 2014-09-18 | B in MTEP15 | B | West | ATC | Rebuild Y-47 Mckenna - Castle Rock 69 kV | Rebuild Y-145 from McKenna - Castle Rock 69 kV with T2 4/0 | 2023-12-31 | 2023-12-31 | 0 | Reliability | 2023-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 8.5 | 2 |  | PR06467 | American Transmission Co. LLC | Bottom-Up | Validated
7764 | 2014-09-18 | B in MTEP15 | B | West | ATC | Rebuild Y-49 Wautoma - Chaffee Creek 69 kV | Rebuild Y-145 from Wautoma - Chaffee Creek 69 kV with T2 4/0 | 2023-12-31 | 2023-12-31 | 0 | Reliability | 2023-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 13.03 | 2 |  | PR06465 | American Transmission Co. LLC | Bottom-Up | Validated
7765 | 2014-09-18 | B in MTEP15 | B | West | ATC | Rebuild Y-145 Lincoln - McKenna 69 kV | Rebuild Y-145 from Lincoln Pumping Station - McKenna 69 kV with T2 4/0 Penguin conductor. | 2023-12-31 | 2023-12-31 | 0 | Reliability | 2023-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 6.61 | 3 |  | PR06467 | American Transmission Co. LLC | Bottom-Up | Validated
8073 | 2014-09-15 | B in MTEP15 | B | West | ATC | Plains - Marquette Area Reinforcement Project | Uprate Plains - Arnold 138 kV line and upgrade existing Plains 345/138 kV transformer and install a 2nd Plains 345/138 kV transformer | 2020-12-01 | 2020-12-01 | 40000000 | Reliability | 2020-12-01 |  | MI | MI | Conceptual |  |  |  | 345 | 138 | 0 | 29 | 3 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8076 | 2015-11-23 | B in MTEP15 | B | West | ATC | Morgan - Plains Area Reinforcement Project | New Thunder Substation, Loop Morgan - Plains 345 into new Thunder Substation, New Morgan - Thunder 138 kV line, Convert Thunder - Crivitz 69 kV to 138 kV. | 2020-12-01 | 2020-12-01 | 96100000 | Reliability | 2020-12-01 |  | WI | WI | Conceptual |  |  |  | 345 | 69 | 102 | 13 | 6 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8082 | 2015-10-01 | B in MTEP15 | B | West | ATC | Green Bay Area Reinforcement Project | Highway V - Preble 138 kV line reconductor | 2020-12-01 | 2020-12-01 | 6000000 | Reliability | 2020-12-01 |  | WI | WI | Conceptual |  |  |  | 138 | 0 | 0 | 2 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8084 | 2014-09-15 | B in MTEP15 | B | West | ATC | Rhinelander Area Reinforcement Project | Uprate Highway 8 - Clear Lake 115 kV line | 2020-12-01 | 2020-12-01 | 24000000 | Reliability | 2020-12-01 |  | WI | WI | Conceptual |  |  |  | 115 | 0 | 0 | 21 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8089 | 2015-01-14 | B in MTEP15 | B | West | ATC | Lakota-Winona 69 kV to 138 kV Conversion and Mass Substation Expansion | Convert the existing 69-kV lines from Conover-Mass and Mass-Winona from 69 kV to 138 kV; Modify the existing Mass Substation to accommodate 138-kV buswork and a new 138/69-kV transformer | 2021-12-01 | 2021-12-01 | 100000000 | Reliability | 2021-12-31 |  | WI,MI | MI | Conceptual |  |  |  | 138 | 69 | 0 | 68.5 | 3 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8263 | 2014-11-04 | B in MTEP15 | B | West | ATC | Rebuild Y-45 W. Wisconsin Rapids - Sigel 69 kV | Rebuild Y-45 on existing right of way. No terminal equipment is being replaced. | 2021-12-31 | 2021-12-31 | 18667906 | Reliability | 2021-12-31 |  | WI | WI | Conceptual |  |  |  | 69 | 0 | 0 | 17.17 | 5 |  | PR06463 FP:4485 WO:601142 | American Transmission Co. LLC | Bottom-Up | Validated
8440 | 2014-11-11 | B in MTEP15 | B | West | ATC | Rebuild Oak Creek- Hayes 138 kV | Asset maintenance, reconductor line 811 Oak Creek - Hayes | 2019-12-31 | 2019-12-31 | 13743440 | Reliability | 2019-12-31 |  | WI | WI | Conceptual |  |  |  | 138 | 0 | 0 | 12.85 | 1 |  | PR04970 | American Transmission Co. LLC | Bottom-Up | Validated
8441 | 2014-11-11 | B in MTEP15 | B | West | ATC | Escanaba Load Addition T-D | Build new Escanaba 69 kV substation with distribution loads | 2016-12-31 | 2016-12-31 | 5616000 | T-D | 2016-12-31 |  | MI | MI | Proposed |  |  |  | 69 | 12.47 | 0 | 0 | 3 |  | PR04202 | American Transmission Co. LLC | Bottom-Up | Validated
8444 | 2015-01-14 | B in MTEP15 | B | West | ATC | Replace First Ave-Sawyer 69 kV (UG) | Asset maintenance, Replace UG Cable from 1st Ave-Sawyer 69 kV line | 2020-12-31 | 2020-12-31 | 0 | Reliability | 2020-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 1 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8620 | 2015-01-07 | B in MTEP15 | B | West | ATC | Construct Howards Grove - Erdman 138 kV | Construct a new 138 kV line from Howards Grove to Erdman | 2018-12-12 | 2018-12-12 | 0 | Reliability | 2018-12-31 |  | WI | WI | Proposed |  |  |  | 138 | 0 | 6.6 | 0 | 1 |  |  | American Transmission Co. LLC | Bottom-Up | Validated
8641 | 2015-01-08 | B in MTEP15 | B | West | ATC | Install Boscobel Capacitor | Project consists of adding a 2nd 8.16 MVAR step | 2023-06-01 | 2023-06-01 | 1394539 | Reliability | 2023-12-31 |  | WI | WI | Proposed |  |  |  | 69 | 0 | 0 | 0 | 1 |  | PR7009 | American Transmission Co. LLC | Bottom-Up | Validated
2632 | 2014-12-19 | B in MTEP15 | B | West | GRE | Onigum 115 kV Conversion | Onigum 115 kV Conversion | 2022-11-30 | 2022-11-30 | 5300000 | 34.5 kV distribution system load serving concerns | 2022-11-30 |  | MN | MN | Proposed | Other | Not Shared | Distribution | 115 | 0 | 0 | 9.45 | 1 | Y | 20385 | Great River Energy | Bottom-Up | Validated
8111 | 2015-05-29 | B in MTEP15 | B | West | ITCM | ITCM Cedar Rapids-North Liberty Area Upgrades | 161 and 69 kV upgrades in the Cear Rapids to North Liberty, IA area including a new North Liberty 161/69kV sub and new Rose Hollow to North Liberty to Fairfax 161kV line. | 2019-12-31 | 2024-12-31 | 74482581.6 | The North Liberty IA area which includes the northern Coralville and Tiffin areas, is experiencing continued load growth. The existing system in the area requires updgrades to support both near term issues and long term projected load growth. Some of the upgrades as part of the comprehensive area plan are non-MISO TO upgrades (CIPCO), but are also needed as part of a complete package of system upgrades. |  |  | IA | IA | Planned | BaseRel |  |  | 161 | 69 | 31.5 | 0 | 9 |  | CR-N Liberty Upgrades | ITC Midwest | Bottom-Up | Validated
8842 | 2015-03-19 | B in MTEP15 | B | West | ITCM | Quad Cities-Rock Creek 345kV Dbl Ckt | Rebuild the Quad Cities to Rock Creek 345kV line to double circuit and add 345kV terminals at both substations. | 2024-12-31 | 2024-12-31 | 0 | Loading on the Quad Cities-Rock Creek 345kV for several N-2 events on the 345kV. | 2019-12-31 |  | IA,IL | IA,IL | Conceptual | BaseRel |  |  | 345 | 0 | 0 | 0 | 1 |  | Quad-Rock Ck 345 | ITC Midwest | Bottom-Up | Validated
8843 | 2015-03-19 | B in MTEP15 | B | West | ITCM | Rock Creek 2nd 345/161kV Transformer | Add a 2nd 345/161kV 450MVA transformer at the Rock Creek substation. | 2024-12-31 | 2024-12-31 | 0 | Several N-2 contingencies overload the existing Rock Creek 345/161kV in 2024. | 2024-12-31 |  | IA | IA | Conceptual | BaseRel |  |  | 345 | 161 | 0 | 0 | 1 |  | Rock Creek 2nd 345/161kV | ITC Midwest | Bottom-Up | Validated
8844 | 2015-03-19 | B in MTEP15 | B | West | ITCM | Albany-Galena 161kV Rebuild | Rebuild the Albany-York-Savanna-Galena 161kV line. | 2024-12-31 | 2024-12-31 | 0 | Several N-2 contingecies will overlaod the Albany-Galena 161kV line in 2024. | 2024-12-31 |  | IL | IL | Conceptual | BaseRel |  |  | 161 | 0 | 0 | 52.85 | 3 |  | Albany-Galena 161kV Rebuild | ITC Midwest | Bottom-Up | Validated
8023 | 2015-04-09 | B in MTEP15 | B | West | MEC | Hills - Sub E 161 kV Reconductor | Reconductor the Hills - Sub E 161 kV line in Iowa City to increase the line rating. |  |  | 4000000 | Compliance. N-1-1 thermal overloads in outer year planning models. | 2019-06-01 |  | IA | IA | Proposed | BaseRel |  |  | 161 | 0 | 0 | 6.6 | 1 |  |  | MidAmerican Energy Company | Bottom-Up | Validated
8114 | 2015-04-09 | B in MTEP15 | B | West | MEC | Sub A - Sub 84 69 kV Line Uprate | Replace structures to allow a higher conductor operating temperature. | 2021-06-01 | 2021-06-01 | 0 | N-1-1 thermal overloads in MTEP14 2024 models. | 2021-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 8.6 | 1 | NT |  | MidAmerican Energy Company | Bottom-Up | Validated
7913 | 2015-05-07 | B in MTEP15 | B | West | MP | 868 Line Upgrade | Increase capacity of Little Falls - West St. Cloud 115 kV Line | 2019-11-01 | 2019-11-01 | 6800000 | Post-contingent loading for multiple outage scenarios | 2019-11-01 |  | MN | MN | Planned | BaseRel |  |  | 115 | 0 | 0 | 17.57 | 1 | Y |  | Minnesota Power (Allete, Inc.) | Bottom-Up | Validated
4237 | 2014-09-12 | B in MTEP15 | B | West | MPC, OTP | Hensel-Drayton 115 kV #2 | Hensel Sub Expansion, Drayton Sub Expansion, Hensel-Drayton 115 kV Transmission Line | 2021-11-15 | 2021-11-15 | 6500000 | Another Source Needed to Support Load Growth in North East North Dakota | 2021-11-15 | Lake Ardoch-Langdon 230 kV, Lake Ardoch-Mandt 115 kV | ND | ND | Proposed | BaseRel |  |  | 115 | 0 | 22 | 0 | 3 | Y | OTP, MPC | Otter Tail Power Company | Bottom-Up | Validated
9001 | 2015-04-28 | B in MTEP15 | B | West | MPW | MPW Terminal upgrade West to Isett (69 kV Line 95) | Upgrade CT limits at Isett and West substations to obtain the 89 MVA conductor rating at both terminals. |  |  | 0 | Facility overloads | 2017-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | MPW-WS-TT-L95 | Muscatine Power & Water (Board Of Water, Electric & Communications) | Bottom-Up | Validated
9021 | 2015-04-28 | B in MTEP15 | B | West | MPW | MPW Terminal upgrade MPW GEN to Pine St (69 kV Line 91) | Upgrade CT limits at Pine ST substation to obtain the 89 MVA conductor rating at both terminals |  |  | 0 | Facility overloads | 2017-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | MPW-PP-PS-L91 | Muscatine Power & Water (Board Of Water, Electric & Communications) | Bottom-Up | Validated
9022 | 2015-04-28 | B in MTEP15 | B | West | MPW | MPW Line Reconductoring Pine St to Isett (69 kV Line 98) | Reconductor MPW Pine St to Isett Line 98 to 89 MVA. |  |  | 0 | Facility overloads. | 2018-06-01 |  | IA | IA | Proposed | Other |  | Reliability | 69 | 0 | 0 | 0 | 1 |  | MPW-PS-TT-L98 | Muscatine Power & Water (Board Of Water, Electric & Communications) | Bottom-Up | Validated
2746 | 2014-08-27 | B in MTEP15 | B | West | OTP | Turtle Lake-Mercer 41.6 kV Line Upgrade | Rebuild Existing 18-Mile 41.6 kV Line | 2020-11-01 | 2020-11-01 | 1000000 | Structure integrity of existing line is leading to reliability concerns | 2020-11-01 |  | ND | ND | Proposed | Other | Not Shared | Distribution | 41.6 | 0 | 0 | 0 | 1 | Y | OTP | Otter Tail Power Company | Bottom-Up | Validated
4236 | 2015-03-20 | B in MTEP15 | B | West | OTP | Ortonville 115/41.6 kV Transformer | Replace Transformer - 40 MVA | 2020-11-15 | 2020-11-15 | 1000000 | Load Growth in Local Area | 2020-11-15 |  | MN | MN | Proposed | Other |  | Reliability | 115 | 41.6 | 0 | 0 | 1 | Y | OTP | Otter Tail Power Company | Bottom-Up | Validated
8085 | 2015-03-20 | B in MTEP15 | B | West | OTP | OTP Kerkhoven Town Conversion to 115 kV Service - 115/12.5 kV | Build a new, approximately, one mile 115 kV line from the GRE Kerkhoven 115/41.6 kV sub to the new OTP Kerkhoven Town substation. Also convert the Kerkhoven town delivery substation from 41.6 kV to 115 kV through the installation of a new 10 MVA 115/12.5 kV transformer. This project will consist of two facilities: 1. New 115/12.5 kV Substation at Kerkhoven Town with a new (1) 115 kV breaker and a new 10 MVA 115/12.5 kV transformer. 2. Approxmetely 1 mile of115 kV transmission line from the GRE Kerkhoven 115 kV Substation to the New Kerkhoven Town 115/12.5 kV substation. The total estimated cost of this project is $ 1.7 million. The expected in service date for this project is November 15, 2020. | 2020-11-15 | 2020-11-15 | 1700000 | Due to the load growth in the area it will be experiencing low voltages. | 2020-11-15 | The other alternative under study was to add 2.1 MVAR of capacitance at OTP Kerkhoven on the 12.5 kV level and 900 kVAR of capacitance at Murdock on the 12.5 kV level. Long term, this alternative will not meet system demands. Other town conversions were also considered. | MN | MN | Proposed | Other |  | Reliability | 115 | 12.5 | 5 | 0 | 2 | Y |  | Otter Tail Power Company | Bottom-Up | Validated